## 153_161
S&C Power Fuses - Type SMD-1A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (69 kV)
Standard Speed (TCC 153-1-6-1) | [9 empty] | Standard Speed (TCC 153-1-6-1) | [9 empty] | Standard Speed (TCC 153-1-6-1) | [9 empty] | Standard Speed (TCC 153-1-6-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
12001.9 | 0.015699 | 12001.9 | 0.015699 | 12001.9 | 0.015699 | 12001.9 | 0.015699 | 12001.9 | 0.015792 | 12001.9 | 0.015792 | 12001.9 | 0.015792 | 12001.9 | 0.015903 | 12001.9 | 0.015903 | 12001.9 | 0.015998 | 12001.9 | 0.016206 | 12001.9 | 0.016498 | 12001.9 | 0.016997 | 12001.9 | 0.017792 | 11187.8 | 0.020193 | 11187.8 | 0.022195 | 11187.8 | 0.023369 | 11194.2 | 0.025132
9450.37 | 0.018005 | 9272.5 | 0.018203 | 9403.23 | 0.018095 | 12001.9 | 0.015699 | 10730.1 | 0.016796 | 10838 | 0.016696 | 11145.7 | 0.016498 | 11462.3 | 0.016302 | 11612.2 | 0.016206 | 10644.6 | 0.017201 | 11101.2 | 0.016997 | 10591.5 | 0.017898 | 11508.2 | 0.017494 | 11145.7 | 0.018791 | 9943.25 | 0.022386 | 10179.4 | 0.024214 | 10179.4 | 0.025656 | 9880.83 | 0.028605
7893.54 | 0.019905 | 7776.01 | 0.020104 | 7901.44 | 0.019905 | 10570.4 | 0.016896 | 9300.36 | 0.018203 | 9403.23 | 0.018095 | 9718.73 | 0.017898 | 10034.7 | 0.017598 | 10186.4 | 0.017494 | 9217.02 | 0.018791 | 9670.25 | 0.018494 | 9161.89 | 0.019708 | 10085 | 0.019206 | 9709.02 | 0.020898 | 8597.59 | 0.025436 | 8637.05 | 0.028409 | 8661.81 | 0.0305 | 8240.97 | 0.035115
6334.64 | 0.022292 | 6277.88 | 0.022403 | 6411.12 | 0.022203 | 9134.44 | 0.018403 | 7869.89 | 0.020004 | 7972.87 | 0.019905 | 8289.98 | 0.019494 | 8611.07 | 0.019301 | 8758.72 | 0.019092 | 7783.79 | 0.020691 | 8240.38 | 0.020406 | 7737.23 | 0.022093 | 8654.24 | 0.021509 | 8281.69 | 0.023708 | 6912.72 | 0.031064 | 6702.29 | 0.0371 | 7244.97 | 0.037635 | 6771.71 | 0.04487
4773.21 | 0.025694 | 4782.77 | 0.025694 | 4913.67 | 0.02539 | 7706.34 | 0.020204 | 6443.26 | 0.022203 | 6547.19 | 0.022093 | 6855.41 | 0.021702 | 7178.14 | 0.021296 | 7330.48 | 0.021191 | 6353.68 | 0.023311 | 6807.58 | 0.022898 | 6303.05 | 0.025289 | 7221.34 | 0.024498 | 6848.55 | 0.027709 | 5233.78 | 0.041176 | 5385.76 | 0.047679 | 5956.7 | 0.04787 | 5523.14 | 0.059035
3215.55 | 0.030786 | 3287.08 | 0.030603 | 3417.82 | 0.03021 | 6277.88 | 0.022492 | 5012.94 | 0.025289 | 5114.21 | 0.025089 | 5425.04 | 0.024595 | 5749.02 | 0.024112 | 5900.46 | 0.023897 | 4923.51 | 0.027003 | 5376.43 | 0.026393 | 4874.51 | 0.030391 | 5795.19 | 0.029005 | 5419.62 | 0.034103 | 3915.26 | 0.058195 | 4395.25 | 0.06273 | 5115.29 | 0.058597 | 4473.95 | 0.080202
1655.27 | 0.040618 | 1793.14 | 0.039582 | 1925.09 | 0.038688 | 4845.35 | 0.025592 | 3582.3 | 0.029793 | 3687.71 | 0.029499 | 3998.86 | 0.028689 | 4318.96 | 0.028097 | 4468.34 | 0.027792 | 3493.85 | 0.0332 | 3947.21 | 0.032193 | 3445.27 | 0.039898 | 4362.37 | 0.036813 | 5338.93 | 0.034683 | 3133.6 | 0.079016 | 3646.95 | 0.082296 | 4254.14 | 0.076434 | 3686.84 | 0.10809
95.067 | 0.094777 | 299.058 | 0.078398 | 429.944 | 0.072481 | 3417.82 | 0.0303 | 2151.1 | 0.037702 | 2256.88 | 0.037218 | 2567.64 | 0.03591 | 2889.24 | 0.034891 | 3037.38 | 0.034409 | 2064.68 | 0.047191 | 2516.8 | 0.044284 | 3397.37 | 0.040416 | 4306.02 | 0.037292 | 5201.9 | 0.035485 | 2538.33 | 0.10809 | 3099.7 | 0.10594 | 3634.45 | 0.096832 | 3019.14 | 0.1493
92.9054 | 0.095628 | 294.311 | 0.079024 | 420.168 | 0.073277 | 1987.69 | 0.038496 | 721.752 | 0.06389 | 826.078 | 0.061707 | 1137.63 | 0.056374 | 1457.84 | 0.052483 | 1607.96 | 0.050993 | 2033.94 | 0.047709 | 2486.77 | 0.044682 | 3277.24 | 0.041598 | 4178.75 | 0.038306 | 5028 | 0.036704 | 2231.55 | 0.13155 | 2595.64 | 0.14027 | 3103.25 | 0.12359 | 2541.24 | 0.20041
88.9949 | 0.096968 | 284.472 | 0.08029 | 403.289 | 0.074896 | 558.173 | 0.068084 | 711.718 | 0.0644 | 813.778 | 0.0622 | 1110.65 | 0.057277 | 1424.69 | 0.053324 | 1579.27 | 0.051604 | 1977.78 | 0.048715 | 2427.8 | 0.045578 | 3161.35 | 0.042984 | 3896.23 | 0.040901 | 4787.55 | 0.038496 | 1867.59 | 0.17578 | 2213.73 | 0.18276 | 2704.87 | 0.15488 | 2182.28 | 0.26127
83.8959 | 0.099208 | 274.962 | 0.081576 | 381.324 | 0.077085 | 544.936 | 0.068901 | 685.179 | 0.065692 | 787.361 | 0.063385 | 1075.67 | 0.058484 | 1344.41 | 0.055485 | 1535.66 | 0.052692 | 1896.43 | 0.050188 | 2351.34 | 0.046678 | 3037.38 | 0.044416 | 3582.3 | 0.044284 | 4554.05 | 0.040497 | 1612.07 | 0.22707 | 1939.51 | 0.22876 | 2332.12 | 0.19836 | 1893.43 | 0.33635
79.406 | 0.1013 | 263.126 | 0.083378 | 360.196 | 0.079575 | 526.718 | 0.070283 | 664.927 | 0.067011 | 755.73 | 0.065108 | 1041.79 | 0.059777 | 1266.11 | 0.058022 | 1476.92 | 0.054124 | 1812.98 | 0.052119 | 2265.92 | 0.048185 | 2924.12 | 0.045988 | 3326.77 | 0.047615 | 4166.23 | 0.044416 | 1370.17 | 0.30271 | 1720.79 | 0.28374 | 2010.74 | 0.25756 | 1623.19 | 0.44916
74.1856 | 0.10405 | 247.554 | 0.086071 | 336.179 | 0.0828 | 508.601 | 0.071693 | 641.415 | 0.068423 | 719.59 | 0.067211 | 997.945 | 0.061585 | 1158.29 | 0.061891 | 1404.89 | 0.056206 | 1714.24 | 0.054502 | 2181.43 | 0.049692 | 2710.11 | 0.049299 | 3064.84 | 0.051809 | 3888.44 | 0.047804 | 1174.61 | 0.40101 | 1451.73 | 0.38746 | 1696.34 | 0.34791 | 1414.81 | 0.58289
68.6874 | 0.10773 | 235.244 | 0.088411 | 299.058 | 0.089116 | 491.107 | 0.073205 | 612.576 | 0.070423 | 674.302 | 0.070074 | 944.538 | 0.064017 | 1077.82 | 0.065627 | 1316.47 | 0.05901 | 1598.34 | 0.057791 | 2081.27 | 0.051707 | 2524.36 | 0.052797 | 2795.45 | 0.05722 | 3585.88 | 0.052275 | 1018.55 | 0.52338 | 1257.42 | 0.50282 | 1481.96 | 0.44737 | 1253.82 | 0.74141
64.1076 | 0.11132 | 219.34 | 0.091903 | 268.441 | 0.095819 | 452.442 | 0.076703 | 580.373 | 0.072914 | 616.263 | 0.074599 | 894.883 | 0.06648 | 987.027 | 0.070283 | 1232.38 | 0.0622 | 1427.55 | 0.063574 | 1958.1 | 0.05461 | 2337.27 | 0.05688 | 2601.24 | 0.06183 | 3336.76 | 0.056711 | 881.216 | 0.68663 | 1051.13 | 0.69933 | 1271.9 | 0.59197 | 1107.35 | 0.95938
59.2377 | 0.11572 | 205.125 | 0.095533 | 237.371 | 0.10488 | 418.072 | 0.080689 | 549.313 | 0.075569 | 572.877 | 0.07871 | 841.924 | 0.069519 | 912.049 | 0.075269 | 1145.62 | 0.066019 | 1303.37 | 0.069312 | 1853.31 | 0.05722 | 2106.39 | 0.063385 | 2442.41 | 0.066612 | 3016.2 | 0.064081 | 822.24 | 0.77839 | 885.768 | 0.97825 | 1114.98 | 0.76689 | 971.291 | 1.2819
53.6003 | 0.12222 | 190.302 | 0.1002 | 212.219 | 0.11469 | 385.928 | 0.084967 | 507.078 | 0.079812 | 535.75 | 0.0828 | 784.217 | 0.073496 | 845.299 | 0.080689 | 1058.59 | 0.070633 | 1198.35 | 0.07512 | 1733.2 | 0.060916 | 1927.02 | 0.069865 | 2290.99 | 0.071765 | 2759.34 | 0.071693 | 733.285 | 0.96544 | 779.607 | 1.2834 | 981.352 | 0.99748 | 850.487 | 1.7636
48.84 | 0.12934 | 176.375 | 0.10541 | 187.282 | 0.12806 | 351.302 | 0.090904 | 471.378 | 0.084211 | 492.583 | 0.088499 | 728.278 | 0.078087 | 779.526 | 0.08719 | 988.015 | 0.07512 | 1110.65 | 0.081172 | 1645.37 | 0.064017 | 1729.73 | 0.079024 | 2136.09 | 0.078165 | 2469.43 | 0.082472 | 644.292 | 1.2622 | 669.101 | 1.8232 | 859.788 | 1.3336 | 777.824 | 2.242
45.2203 | 0.13633 | 160.711 | 0.11255 | 170.138 | 0.1406 | 317.869 | 0.098033 | 439.948 | 0.088763 | 447.044 | 0.096105 | 674.302 | 0.083378 | 708.168 | 0.0962 | 904.781 | 0.081738 | 1019.12 | 0.089028 | 1532.59 | 0.068627 | 1558.87 | 0.089738 | 1963.98 | 0.087017 | 2272.73 | 0.092636 | 556.459 | 1.7485 | 594.668 | 2.4997 | 776.045 | 1.7178 | 708.119 | 2.9905
41.5767 | 0.14514 | 147.467 | 0.12029 | 151.806 | 0.15855 | 289.06 | 0.10604 | 398.478 | 0.096105 | 398.877 | 0.10678 | 634.397 | 0.088235 | 655.683 | 0.10416 | 830.219 | 0.089116 | 932.337 | 0.098423 | 1460.76 | 0.072194 | 1427.55 | 0.1003 | 1794.94 | 0.097838 | 2046.18 | 0.1072 | 510.084 | 2.1563 | 540.447 | 3.396 | 698.456 | 2.29 | 643.923 | 4.3844
37.62 | 0.15714 | 130.398 | 0.13378 | 139.296 | 0.17476 | 263.916 | 0.11481 | 365.639 | 0.10374 | 353.77 | 0.12005 | 595.661 | 0.093376 | 605.875 | 0.11378 | 753.466 | 0.098619 | 856.36 | 0.10881 | 1390.91 | 0.076021 | 1308.59 | 0.113 | 1670.24 | 0.10795 | 1879.44 | 0.12125 | 452.562 | 3.0025 | 498.822 | 4.7531 | 630.066 | 3.1218 | 589.583 | 6.7139
34.6928 | 0.16896 | 115.884 | 0.14923 | 123.42 | 0.20264 | 240.718 | 0.12517 | 330.512 | 0.11401 | 315.337 | 0.13606 | 551.515 | 0.1004 | 540.593 | 0.13024 | 686.55 | 0.10946 | 778.747 | 0.12222 | 1321.75 | 0.08029 | 1195.96 | 0.12781 | 1565.12 | 0.11828 | 1719.39 | 0.13865 | 411.299 | 4.0955 | 470.258 | 6.4574 | 571.635 | 4.3494 | 556.459 | 9.6866
31.8019 | 0.18366 | 103.294 | 0.16795 | 108.591 | 0.23921 | 219.779 | 0.13728 | 296.082 | 0.1273 | 283.053 | 0.15405 | 497.036 | 0.11188 | 494.063 | 0.146 | 641.415 | 0.11851 | 712.43 | 0.13701 | 1239.8 | 0.086328 | 1093.02 | 0.14586 | 1424.69 | 0.13552 | 1577.69 | 0.15855 | 370.601 | 6.4095 | 444.347 | 9.2686 | 530.029 | 6.1225 | 530.637 | 14.3649
28.8331 | 0.20325 | 92.627 | 0.18941 | 97.8645 | 0.27682 | 201.465 | 0.15057 | 268.173 | 0.14186 | 251.295 | 0.17827 | 460.199 | 0.12162 | 453.801 | 0.1627 | 599.846 | 0.12857 | 642.056 | 0.15792 | 1180.51 | 0.091176 | 952.125 | 0.17863 | 1315.15 | 0.15253 | 1424.69 | 0.18679 | 345.007 | 10.4353 | 424.455 | 13.5188 | 491.733 | 9.5543 | 507.753 | 22.9497
26.8837 | 0.22049 | 83.6445 | 0.21381 | 88.1093 | 0.32321 | 185.975 | 0.16514 | 245.581 | 0.15683 | 230.356 | 0.20024 | 416.82 | 0.13674 | 421.009 | 0.18041 | 547.667 | 0.14442 | 583.282 | 0.18113 | 1117.33 | 0.097354 | 867.566 | 0.20691 | 1211.61 | 0.17218 | 1300.77 | 0.21702 | 331.455 | 15.1943 | 405.918 | 21.2542 | 470.528 | 13.7137 | 493.991 | 35.083
24.5943 | 0.24547 | 72.2093 | 0.25925 | 78.9309 | 0.38267 | 171.848 | 0.18113 | 226.02 | 0.17321 | 211.372 | 0.22581 | 384.387 | 0.15072 | 390.587 | 0.20044 | 512.687 | 0.15745 | 533.611 | 0.2065 | 1049.11 | 0.10551 | 791.307 | 0.24016 | 1097.4 | 0.20084 | 1198.35 | 0.24989 | 317.343 | 25.8533 | 394.916 | 31.2321 | 452.562 | 20.7016 | 489.486 | 47.635
22.6127 | 0.27408 | 61.9645 | 0.32225 | 70.0751 | 0.46354 | 156.743 | 0.20365 | 206.979 | 0.19378 | 195.511 | 0.25264 | 352.71 | 0.16795 | 354.478 | 0.2308 | 473.268 | 0.17598 | 485.249 | 0.2385 | 990.983 | 0.11345 | 729.006 | 0.2749 | 977.206 | 0.2428 | 1128.56 | 0.27709 | 309.626 | 44.1664 | 388.859 | 40.5071 | 441.052 | 29.9189 | 483.914 | 75.4947
20.3994 | 0.3156 | 55.2327 | 0.38305 | 62.9639 | 0.5532 | 145.707 | 0.2247 | 188.597 | 0.22028 | 173.228 | 0.3024 | 323.967 | 0.18828 | 333.5 | 0.25339 | 436.879 | 0.19728 | 442.154 | 0.27599 | 902.071 | 0.12806 | 680.399 | 0.30847 | 885.978 | 0.28632 | 1064.96 | 0.30817 | 304.877 | 74.9776 | 383.552 | 59.6257 | 433.046 | 46.9578 | 483.36 | 120.404
18.8121 | 0.35662 | 50.2269 | 0.4446 | 55.5096 | 0.68764 | 134.639 | 0.25064 | 168.108 | 0.25925 | 153.332 | 0.36777 | 297.269 | 0.21212 | 310.642 | 0.28265 | 404.5 | 0.22071 | 389.807 | 0.34001 | 840.242 | 0.14074 | 641.415 | 0.3417 | 795.274 | 0.34341 | 1004.95 | 0.34341 | 301.924 | 128.602 | 377.669 | 88.3227 | 429.097 | 67.9045 | 482.807 | 183.009
17.6634 | 0.39464 | 46.2724 | 0.50689 | 50.1265 | 0.82308 | 123.915 | 0.28153 | 150.145 | 0.30725 | 140.274 | 0.42474 | 273.591 | 0.23897 | 286.184 | 0.32098 | 374.521 | 0.24816 | 362.726 | 0.38496 | 788.148 | 0.15405 | 596.854 | 0.38726 | 727.55 | 0.39937 | 952.125 | 0.38116 | 300.889 | 197.043 | 373.156 | 125.258 | 426.16 | 98.8157 | 482.807 | 272.334
16.6348 | 0.43672 | 43.2736 | 0.56767 | 45.2203 | 0.98619 | 115.537 | 0.31248 | 138.739 | 0.34614 | 127.179 | 0.50288 | 245.827 | 0.28069 | 261.813 | 0.37107 | 350.951 | 0.27517 | 337.189 | 0.43542 | 725.37 | 0.1739 | 561.532 | 0.42899 | 685.864 | 0.44416 | 880.678 | 0.44108 | 300.2 | 280.246 | 371.451 | 170.951 | 425.428 | 152.013 | 483.083 | 383.576
15.666 | 0.48812 | 40.835 | 0.62509 | 41.9946 | 1.1333 | 106.76 | 0.35169 | 130.138 | 0.38267 | 119.892 | 0.55375 | 217.81 | 0.33765 | 241.441 | 0.42474 | 323.643 | 0.31279 | 320.423 | 0.47757 | 666.925 | 0.19728 | 530.949 | 0.47238 | 649.808 | 0.48522 | 831.881 | 0.4925 | 299.514 | 418.466 | 368.908 | 233.715 | 423.97 | 230.657 | 483.637 | 519.025
14.7979 | 0.54394 | 38.5339 | 0.689 | 39.4699 | 1.2717 | 98.7493 | 0.39779 | 123.173 | 0.41639 | 112.91 | 0.60916 | 197.871 | 0.39543 | 212.432 | 0.52587 | 302.971 | 0.34891 | 305.405 | 0.52016 | 577.478 | 0.24644 | 509.11 | 0.51094 | 616.263 | 0.53483 | 784.217 | 0.55485 | 299 | 565.263 | 366.382 | 328.241 | 423.242 | 323.019 | 483.914 | 597.556
14.2035 | 0.59245 | 35.8568 | 0.78165 | 37.3202 | 1.4214 | 90.6114 | 0.45669 | 116.932 | 0.45352 | 106.653 | 0.67277 | 175.671 | 0.48281 | 192.215 | 0.62696 | 274.138 | 0.41268 | 294.017 | 0.55872 | 504.044 | 0.30786 | 489.636 | 0.55101 | 587.38 | 0.58543 | 740.024 | 0.62385 | 299.171 | 599.27 | 363.874 | 435.834 | 423.727 | 489.571
13.4972 | 0.66282 | 33.466 | 0.88235 | 35.9645 | 1.5298 | 83.4774 | 0.52275 | 111.006 | 0.49594 | 98.3551 | 0.77623 | 157.056 | 0.58776 | 175.495 | 0.73569 | 253.567 | 0.47285 | 278.004 | 0.6183 | 456.989 | 0.36305 | 470.436 | 0.59186 | 551.515 | 0.66019 | 701.823 | 0.69519 |  |  | 362.626 | 541.186 | 423.242 | 597.556
12.7877 | 0.75045 | 31.6433 | 0.97741 | 34.4852 | 1.6663 | 78.5372 | 0.58137 | 104.646 | 0.54664 | 92.7197 | 0.86672 | 143.251 | 0.68969 | 161.516 | 0.8522 | 231.048 | 0.5554 | 267.102 | 0.66745 | 409.384 | 0.43977 | 440.388 | 0.67144 | 520.956 | 0.73862 | 669.598 | 0.76703 |  |  | 362.211 | 597.214
11.9709 | 0.87711 | 29.6518 | 1.099 | 33.2325 | 1.7987 | 74.7815 | 0.63574 | 99.5425 | 0.5954 | 85.9338 | 0.99603 | 129.101 | 0.83544 | 150.747 | 0.96679 | 211.372 | 0.64785 | 257.657 | 0.71622 | 381.706 | 0.49841 | 417.655 | 0.74822 | 490.126 | 0.83544 | 626.203 | 0.88499
11.3984 | 1 | 27.2355 | 1.2819 | 31.9614 | 1.9611 | 69.7256 | 0.71765 | 93.7453 | 0.66217 | 81.9882 | 1.0924 | 120.132 | 0.95439 | 140.836 | 1.1044 | 188.597 | 0.79733 | 246.812 | 0.77777 | 361.278 | 0.54828 | 389.417 | 0.86328 | 461.121 | 0.94589 | 597.451 | 0.9813
10.9077 | 1.1344 | 25.3941 | 1.4615 | 30.862 | 2.1149 | 65.7963 | 0.79733 | 86.2783 | 0.76703 | 77.5228 | 1.2173 | 112.797 | 1.0773 | 131.314 | 1.2617 | 173.401 | 0.94027 | 234.54 | 0.86071 | 343.657 | 0.59955 | 367.472 | 0.9745 | 439.069 | 1.0478 | 561.532 | 1.13
10.4695 | 1.2883 | 23.8913 | 1.6383 | 29.7112 | 2.2989 | 62.3998 | 0.87624 | 79.8839 | 0.88148 | 73.3006 | 1.362 | 106.228 | 1.2065 | 123.05 | 1.437 | 163.794 | 1.0509 | 221.323 | 0.97064 | 330.182 | 0.64785 | 347.459 | 1.0957 | 423.967 | 1.1344 | 530.419 | 1.2883
10.1094 | 1.4413 | 22.6806 | 1.8077 | 28.7754 | 2.4792 | 58.7657 | 0.98521 | 74.5575 | 1.003 | 70.2154 | 1.4923 | 101.553 | 1.3233 | 116.815 | 1.6014 | 153.792 | 1.1958 | 208.225 | 1.1033 | 314.078 | 0.71267 | 327.223 | 1.2455 | 407.75 | 1.243 | 504.044 | 1.4543
9.8009 | 1.6029 | 21.6176 | 1.9866 | 27.6747 | 2.7056 | 56.1236 | 1.0806 | 69.8652 | 1.1367 | 66.724 | 1.6629 | 96.5039 | 1.4702 | 109.902 | 1.833 | 145.271 | 1.3472 | 198.466 | 1.2222 | 297.864 | 0.78788 | 310.021 | 1.406 | 394.908 | 1.3299 | 485.734 | 1.5887
9.3977 | 1.8586 | 20.7699 | 2.1594 | 26.5364 | 2.9971 | 53.7613 | 1.1781 | 65.5337 | 1.287 | 63.3429 | 1.8679 | 92.9054 | 1.5887 | 104.646 | 2.0365 | 136.947 | 1.5344 | 190.302 | 1.3378 | 283.904 | 0.865 | 296.378 | 1.5543 | 382.088 | 1.4327 | 472.322 | 1.7082
9.1291 | 2.0732 | 19.8758 | 2.3684 | 25.5214 | 3.2807 | 51.6532 | 1.2768 | 62.1506 | 1.4313 | 60.4345 | 2.0753 | 89.0839 | 1.7442 | 98.947 | 2.3195 | 130.66 | 1.7031 | 183.023 | 1.4688 | 268.71 | 0.96583 | 282.205 | 1.7581 | 367.105 | 1.5792 | 456.076 | 1.8772
8.8859 | 2.3357 | 19.1347 | 2.5771 | 24.6189 | 3.591 | 49.6774 | 1.3838 | 58.8245 | 1.6045 | 57.7173 | 2.3195 | 85.5052 | 1.9073 | 93.2777 | 2.6577 | 124.411 | 1.9073 | 176.198 | 1.6029 | 256.629 | 1.0593 | 270.598 | 1.9455 | 354.478 | 1.7252 | 439.509 | 2.0691
8.7099 | 2.5873 | 18.366 | 2.8349 | 23.8435 | 3.9152 | 47.5864 | 1.5147 | 55.7878 | 1.7916 | 55.1775 | 2.5951 | 81.2536 | 2.1445 | 89.7995 | 2.9178 | 118.699 | 2.1445 | 170.82 | 1.7338 | 244.601 | 1.1688 | 263.126 | 2.096 | 341.943 | 1.8865 | 421.009 | 2.3264
8.5034 | 2.9499 | 17.7342 | 3.0816 | 23.162 | 4.2264 | 45.0848 | 1.6862 | 53.12 | 1.9866 | 52.7494 | 2.912 | 77.4453 | 2.4088 | 85.0787 | 3.3399 | 113.023 | 2.428 | 165.109 | 1.8847 | 232.671 | 1.3011 | 254.584 | 2.2898 | 330.512 | 2.0589 | 406.935 | 2.5592
8.3183 | 3.3498 | 17.1585 | 3.3365 | 22.0764 | 4.8329 | 43.2736 | 1.8513 | 50.4282 | 2.2203 | 50.8333 | 3.2321 | 73.8156 | 2.6949 | 80.6867 | 3.8573 | 108.049 | 2.7191 | 160.39 | 2.0204 | 223.547 | 1.4313 | 246.812 | 2.5139 | 318.187 | 2.2807 | 393.725 | 2.8209
8.1292 | 3.9113 | 16.5352 | 3.6595 | 21.3811 | 5.3165 | 41.2042 | 2.0548 | 47.9207 | 2.494 | 48.645 | 3.674 | 70.992 | 2.9764 | 76.2923 | 4.5083 | 103.605 | 3.0542 | 155.183 | 2.2115 | 212.644 | 1.6029 | 239.757 | 2.7326 | 304.795 | 2.5669 | 379.802 | 3.1279
8.0082 | 4.4152 | 15.9027 | 4.0457 | 20.7699 | 5.8195 | 39.3123 | 2.2807 | 45.3108 | 2.8406 | 46.9718 | 4.1105 | 68.2765 | 3.3003 | 73.5945 | 5.0288 | 99.7418 | 3.4103 | 150.295 | 2.4088 | 204.51 | 1.7598 | 231.51 | 3.018 | 295.786 | 2.8209 | 368.576 | 3.4375
7.8653 | 5.069 | 15.3251 | 4.4771 | 20.2368 | 6.3133 | 37.7708 | 2.4965 | 43.534 | 3.1529 | 45.3561 | 4.6171 | 65.1416 | 3.7589 | 70.992 | 5.6262 | 96.1186 | 3.8116 | 144.691 | 2.6709 | 196.687 | 1.9359 | 224.443 | 3.3167 | 284.188 | 3.1812 | 359.476 | 3.7552
7.7559 | 5.831 | 14.9019 | 4.8473 | 19.6977 | 6.9244 | 35.8927 | 2.8069 | 41.7852 | 3.4856 | 43.7523 | 5.2171 | 62.901 | 4.1309 | 68.4817 | 6.3511 | 93.1845 | 4.2474 | 139.574 | 2.9793 | 189.732 | 2.1254 | 216.29 | 3.685 | 277.448 | 3.4787 | 349.899 | 4.1391
7.6405 | 6.7011 | 14.447 | 5.3377 | 19.2691 | 7.4896 | 34.6235 | 3.0512 | 40.1065 | 3.8765 | 42.1208 | 5.948 | 60.9199 | 4.5488 | 66.3248 | 7.1551 | 90.5208 | 4.7332 | 134.236 | 3.3531 | 181.565 | 2.3921 | 209.478 | 4.0901 | 268.441 | 3.8997 | 343.314 | 4.4771
7.5342 | 7.5945 | 14.034 | 5.8776 | 18.8121 | 8.2308 | 33.4995 | 3.3003 | 38.4953 | 4.3198 | 40.7534 | 6.7344 | 58.7657 | 5.0942 | 64.4934 | 8.013 | 88.1093 | 5.3059 | 128.714 | 3.823 | 173.401 | 2.7137 | 204.92 | 4.446 | 263.916 | 4.2517 | 336.179 | 4.8957
7.4444 | 8.7277 | 13.6465 | 6.5367 | 18.3843 | 9.0274 | 32.5419 | 3.5379 | 37.0228 | 4.8138 | 39.5094 | 7.6021 | 57.2002 | 5.5872 | 62.8381 | 8.9738 | 85.4197 | 6.0553 | 125.16 | 4.2432 | 166.103 | 3.0572 | 199.86 | 4.8666 | 257.657 | 4.705 | 329.192 | 5.3749
7.3703 | 10.2006 | 13.4031 | 7.0493 | 18.0744 | 9.8325 | 31.454 | 3.8496 | 35.8927 | 5.2483 | 38.4953 | 8.522 | 55.6207 | 6.183 | 60.9199 | 10.2922 | 83.3106 | 6.8627 | 122.314 | 4.6354 | 160.069 | 3.4341 | 195.511 | 5.3112 | 252.808 | 5.1758 | 322.029 | 5.9599
7.3042 | 12.2341 | 13.0721 | 7.8087 | 17.752 | 10.7307 | 30.3721 | 4.2306 | 35.0415 | 5.6039 | 37.5073 | 9.5914 | 54.139 | 6.7881 | 59.5347 | 11.7342 | 80.7675 | 8.1982 | 119.652 | 5.1655 | 154.718 | 3.8306 | 191.065 | 5.9127 | 248.298 | 5.7619 | 316.6 | 6.5172
7.2388 | 14.6877 | 12.7239 | 8.7017 | 17.4877 | 11.6645 | 29.3861 | 4.6308 | 34.1763 | 6.0493 | 36.6544 | 10.6669 | 52.8022 | 7.4822 | 58.6483 | 13.2198 | 78.6158 | 9.716 | 117.166 | 5.7964 | 150.446 | 4.1722 | 187.282 | 6.4914 | 243.137 | 6.4978 | 310.952 | 7.1765
7.1883 | 17.5284 | 12.447 | 9.6967 | 17.2791 | 12.8189 | 28.4322 | 5.1094 | 33.3991 | 6.5302 | 36.0366 | 11.8396 | 51.6016 | 8.2472 | 57.5444 | 15.3134 | 76.5215 | 11.7576 | 114.273 | 6.5954 | 147.467 | 4.5038 | 183.39 | 7.2409 | 237.134 | 7.4599 | 304.795 | 7.9259
7.1382 | 21.2749 | 12.1883 | 10.9134 | 17.0559 | 14.214 | 27.2627 | 5.7391 | 32.7378 | 7.0004 | 35.5 | 13.0891 | 50.681 | 9.0454 | 56.5178 | 18.1486 | 74.6321 | 14.2423 | 112.571 | 7.3715 | 144.691 | 4.8425 | 179.938 | 8.0369 | 232.671 | 8.4294 | 297.864 | 9.1176
7.1382 | 24.8409 | 11.9589 | 12.6544 | 16.8693 | 15.7297 | 26.5364 | 6.2323 | 31.9614 | 7.6172 | 35.0064 | 15.042 | 49.8267 | 9.9603 | 55.6207 | 22.1373 | 72.935 | 17.7916 | 110.012 | 8.59 | 142.252 | 5.2431 | 176.375 | 9.0095 | 228.292 | 9.5628 | 292.258 | 10.2209
7.1168 | 30.3004 | 11.8281 | 13.9482 | 16.6847 | 17.6157 | 25.8037 | 6.7881 | 31.3912 | 8.1982 | 34.4852 | 17.9514 | 49.1831 | 10.8702 | 54.9572 | 26.5768 | 71.993 | 20.0241 | 107.941 | 9.9011 | 139.854 | 5.6993 | 173.922 | 10.0198 | 223.995 | 11.0663 | 286.757 | 11.6182
7.1025 | 36.9599 | 11.687 | 15.6207 | 16.5352 | 19.8064 | 25.1665 | 7.335 | 30.7696 | 8.8411 | 34.1421 | 20.4462 | 48.2574 | 12.3809 | 54.5738 | 32.2573 | 71.3479 | 22.6039 | 105.803 | 11.4578 | 137.496 | 6.2509 | 170.649 | 11.2436 | 219.779 | 12.8061 | 281.36 | 13.4182
7.0955 | 50.0888 | 11.5939 | 17.5284 | 16.3871 | 22.2917 | 24.6929 | 7.9024 | 30.1904 | 9.7257 | 33.8024 | 24.3765 | 47.3018 | 14.3559 | 54.5738 | 39.8186 | 70.4263 | 26.5504 | 103.916 | 13.4449 | 135.043 | 6.9727 | 167.94 | 12.6042 | 215.427 | 15.2073 | 276.617 | 15.3591
7.0671 | 63.8904 | 11.513 | 19.8261 | 16.2565 | 25.2891 | 24.2281 | 8.4798 | 29.7409 | 10.426 | 33.6001 | 28.6325 | 46.5975 | 16.5965 | 54.5738 | 49.1035 | 69.7953 | 30.5119 | 101.96 | 16.3186 | 132.502 | 7.7932 | 165.771 | 14.0456 | 210.739 | 18.2027 | 272.226 | 17.4243
7.0601 | 90.0953 | 11.4556 | 22.1373 | 16.1431 | 28.6894 | 23.8435 | 9.1903 | 29.2688 | 11.4692 | 33.533 | 33.7319 | 45.8578 | 19.7083 | 54.5738 | 65.1077 | 69.17 | 35.3792 | 99.443 | 21.2538 | 130.529 | 8.6586 | 163.466 | 15.5124 | 206.359 | 22.8296 | 267.905 | 20.0639
7.0601 | 116.182 | 11.3756 | 25.5669 | 16.0465 | 32.0974 | 23.465 | 10.0099 | 28.9776 | 12.3195 | 33.466 | 39.2687 | 45.4469 | 23.3804 | 54.5738 | 85.5596 | 68.4817 | 43.4992 | 98.0604 | 25.5669 | 128.457 | 9.7064 | 161.355 | 17.4937 | 202.678 | 28.5473 | 262.337 | 24.2316
7.053 | 163.186 | 11.3529 | 30.0009 | 15.9346 | 37.2547 | 23.0695 | 10.9678 | 28.7179 | 13.3385 | 33.2991 | 47.1907 | 44.9947 | 27.4625 | 54.5738 | 123.563 | 67.8681 | 54.2856 | 96.9876 | 30.0606 | 126.544 | 10.8918 | 159.43 | 19.7475 | 199.062 | 34.9253 | 258.69 | 27.7918
7.053 | 213.172 | 11.3416 | 34.6144 | 15.8868 | 42.9411 | 22.7943 | 11.8632 | 28.347 | 15.2375 | 33.1661 | 57.1066 | 44.5916 | 32.8719 | 54.5738 | 169.969 | 67.3273 | 67.7467 | 95.7349 | 36.8133 | 124.91 | 12.1012 | 157.528 | 22.4027 | 195.706 | 45.9418 | 255.093 | 32.1293
7.053 | 316.542 | 11.3416 | 40.7388 | 15.8551 | 49.4461 | 22.5224 | 12.9855 | 28.2904 | 17.4763 | 33.0668 | 69.1748 | 44.3691 | 39.0353 | 54.5738 | 228.069 | 66.8576 | 88.4108 | 94.972 | 43.0692 | 123.173 | 13.9899 | 155.805 | 26.0282 | 192.6 | 59.2446 | 251.547 | 37.107
7.053 | 409.823 | 11.3416 | 49.5937 | 15.8551 | 57.6194 | 22.276 | 14.1015 | 28.2904 | 20.2642 | 32.9677 | 84.7139 | 44.1478 | 49.3971 | 54.5738 | 306.029 | 66.3248 | 117.342 | 93.8391 | 52.7965 | 121.339 | 16.0613 | 154.1 | 29.236 | 189.732 | 75.644 | 248.049 | 42.8984
7.053 | 484.254 | 11.3416 | 59.8955 | 15.8393 | 69.1061 | 22.1206 | 15.4817 | 28.2904 | 24.1595 | 32.9019 | 98.2278 | 44.0596 | 60.1937 | 54.5193 | 429.411 | 66.1262 | 161.252 | 92.9983 | 67.2105 | 119.892 | 18.7907 | 152.262 | 34.3746 | 187.282 | 94.9657 | 245.09 | 48.4735
7.053 | 543.396 | 11.3416 | 74.6735 | 15.8393 | 82.145 | 21.9883 | 17.0476 | 28.2904 | 28.8036 | 32.9019 | 120.054 | 44.0596 | 76.7033 | 54.5193 | 520.674 | 65.8622 | 210.437 | 91.9809 | 85.9857 | 118.343 | 21.9839 | 150.446 | 40.8604 | 184.678 | 124.301 | 242.167 | 56.3179
7.053 | 600.146 | 11.3416 | 93.7472 | 15.8393 | 100.497 | 21.8786 | 18.7347 | 28.2904 | 35.0295 | 32.9019 | 146.877 | 44.0156 | 103.846 | 54.5193 | 577.34 | 65.8622 | 270.563 | 91.3392 | 104.987 | 117.166 | 25.415 | 148.502 | 53.5359 | 182.657 | 159.341 | 239.039 | 64.5282
|  | 11.3416 | 118.749 | 15.8393 | 118.161 | 21.8786 | 21.0228 | 28.2904 | 45.4877 | 32.9019 | 184.393 | 43.9716 | 130.761 | 54.5193 | 600.146 | 65.8622 | 332.66 | 90.7928 | 126.67 | 116.116 | 29.6454 | 147.319 | 64.1447 | 181.202 | 207.119 | 235.951 | 76.7033
|  | 11.3416 | 149.082 | 15.8393 | 138.104 | 21.8786 | 23.6843 | 28.2904 | 58.951 | 32.9019 | 229.432 | 43.796 | 176.508 |  |  | 65.8622 | 414.738 | 90.34 | 155.124 | 114.846 | 35.8747 | 146.145 | 76.4751 | 179.938 | 258.735 | 233.37 | 88.851
|  | 11.3302 | 202.24 | 15.8393 | 163.024 | 21.8786 | 27.8194 | 28.2904 | 74.6735 | 32.9019 | 271.64 | 43.7523 | 238.732 |  |  | 65.8622 | 491.523 | 89.7995 | 201.638 | 113.93 | 42.8133 | 144.836 | 98.1303 | 178.683 | 326.117 | 230.817 | 101.602
|  | 11.3302 | 258.992 | 15.8393 | 201.838 | 21.8786 | 32.4179 | 28.2904 | 86.844 | 32.9019 | 367.037 | 43.6649 | 305.422 |  |  | 65.8622 | 565.983 | 89.3516 | 255.669 | 113.023 | 51.964 | 143.969 | 115.492 | 177.436 | 415.15 | 228.063 | 122.22
|  | 11.3302 | 319.702 | 15.8393 | 248.162 | 21.8786 | 38.6111 | 28.2904 | 108.163 | 32.9019 | 453.524 | 43.6212 | 375.52 |  |  | 65.8622 | 600.146 | 88.7283 | 336.315 | 112.459 | 61.2188 | 142.822 | 141.155 | 176.375 | 498.902 | 225.794 | 146.877
|  | 11.3302 | 399.771 | 15.8393 | 305.725 | 21.8786 | 45.8051 | 28.2904 | 129.726 | 32.9019 | 529.541 | 43.4471 | 473.786 |  |  |  |  | 88.2857 | 422.64 | 111.563 | 74.9708 | 142.252 | 170.815 | 175.846 | 559.277 | 223.547 | 178.27
|  | 11.3302 | 489.088 | 15.8393 | 366.673 | 21.8786 | 56.7673 | 28.2904 | 164.651 | 32.9019 | 573.34 | 43.3602 | 550.458 |  |  |  |  | 87.8454 | 513.993 | 111.228 | 87.1032 | 141.826 | 216.372 | 175.144 | 600.146 | 221.323 | 209.187
|  | 11.3302 | 571.634 | 15.8393 | 436.29 | 21.8786 | 68.4231 | 28.2904 | 205.684 | 32.9019 | 600.146 | 43.2736 | 600.146 |  |  |  |  | 87.6699 | 578.488 | 110.674 | 106.035 | 141.684 | 278.747 |  |  | 219.999 | 251.638
|  | 11.3302 | 600.146 | 15.8393 | 503.882 | 21.8786 | 80.1302 | 28.2904 | 248.409 | [8 empty] | 87.4947 | 600.146 | 110.232 | 127.554 | 141.26 | 359.46 |  |  | 218.683 | 299.117
|  |  |  | 15.8234 | 573.91 | 21.8786 | 94.3076 | 28.2904 | 301.803 | [10 empty] | 109.902 | 173.897 | 141.26 | 461.247 |  |  | 217.592 | 362.328
|  |  |  | 15.8234 | 600.146 | 21.8786 | 113.897 | 28.2904 | 377.765 | [10 empty] | 109.572 | 223.583 | 141.26 | 569.367 |  |  | 216.29 | 446.816
[6 empty] | 21.8786 | 134.984 | 28.2904 | 467.242 | [10 empty] | 109.353 | 282.651 | 141.118 | 600.146 |  |  | 215.427 | 553.749
[6 empty] | 21.8786 | 156.052 | 28.2904 | 552.65 | [10 empty] | 108.917 | 347.868 |  |  |  |  | 214.567 | 600.146
[6 empty] | 21.8786 | 186.419 | 28.2904 | 600.146 | [10 empty] | 108.482 | 424.744
[6 empty] | 21.8786 | 222.917 | [12 empty] | 108.157 | 488.117
[6 empty] | 21.8786 | 282.37 | [12 empty] | 107.833 | 568.802
[6 empty] | 21.8786 | 346.833 | [12 empty] | 107.725 | 600.146
[6 empty] | 21.8786 | 423.901
[6 empty] | 21.8786 | 500.391
[6 empty] | 21.8786 | 564.86
[6 empty] | 21.8786 | 600.146