## 176_161
S&C Power Fuses - Type SMD-1A (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (69 kV)
Very Slow Speed (TCC 176-1-6-1) | [9 empty] | Very Slow Speed (TCC 176-1-6-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
12001.9 | 0.016997 | 12001.9 | 0.017703 | 12001.9 | 0.018903 | 12001.9 | 0.02181 | 11618.6 | 0.025722 | 11618.6 | 0.031164 | 11618.6 | 0.035391 | 11605.3 | 0.0421
11496.7 | 0.017494 | 11079.1 | 0.018791 | 11101.2 | 0.020204 | 10773.1 | 0.024304 | 10668.6 | 0.028418 | 10897 | 0.033767 | 10505 | 0.040538 | 10928.2 | 0.045826
10064.9 | 0.019301 | 9650.93 | 0.020898 | 9679.93 | 0.022694 | 9337.63 | 0.028097 | 9267.17 | 0.033864 | 9679.27 | 0.039529 | 9072.93 | 0.050369 | 9768.34 | 0.054451
8628.31 | 0.021509 | 8215.7 | 0.023708 | 8248.63 | 0.02621 | 8998.44 | 0.029294 | 8142.48 | 0.039916 | 8548.51 | 0.046942 | 8008.42 | 0.060957 | 8711.54 | 0.064959
7199.7 | 0.024498 | 6787.19 | 0.027792 | 6814.39 | 0.031497 | 8491.35 | 0.03131 | 7056.67 | 0.048584 | 7575.82 | 0.05613 | 6920.64 | 0.076964 | 7632.41 | 0.080206
5772.06 | 0.029005 | 5354.97 | 0.034306 | 6659.44 | 0.032193 | 7893.54 | 0.0339 | 6253.73 | 0.057562 | 6709.97 | 0.067231 | 6070.3 | 0.094811 | 6610.83 | 0.10075
4340.61 | 0.036887 | 5222.75 | 0.035204 | 6417.54 | 0.033498 | 7243.03 | 0.037515 | 5589.95 | 0.067734 | 6046.02 | 0.078975 | 5203.9 | 0.12305 | 5912.53 | 0.12193
4250.4 | 0.037515 | 5007.93 | 0.036595 | 6092.34 | 0.035309 | 6706.23 | 0.041186 | 4914.35 | 0.081736 | 5395.01 | 0.094162 | 4638.25 | 0.15054 | 5281.94 | 0.14755
4137.17 | 0.038496 | 4716.27 | 0.038803 | 5726.06 | 0.037702 | 6080.16 | 0.046493 | 4278.56 | 0.10121 | 4814.1 | 0.11337 | 4101.09 | 0.18759 | 4737.55 | 0.17847
3982.9 | 0.039819 | 4441.6 | 0.041309 | 5349.62 | 0.040618 | 5573.52 | 0.052119 | 3750.71 | 0.12482 | 4312.99 | 0.13665 | 3678.41 | 0.22924 | 4244.41 | 0.2171
3758.45 | 0.042013 | 4116.54 | 0.044504 | 4938.3 | 0.044416 | 5068.39 | 0.059127 | 3276.7 | 0.15607 | 3846.39 | 0.16566 | 3276.7 | 0.28418 | 3796.07 | 0.2653
3518.39 | 0.044815 | 3830.55 | 0.048185 | 4540.41 | 0.048909 | 4674.01 | 0.066282 | 2923.88 | 0.18942 | 3461.82 | 0.19967 | 2895.56 | 0.35574 | 3446.01 | 0.31686
3296.96 | 0.047804 | 3500.84 | 0.053218 | 4216.53 | 0.053377 | 4182.93 | 0.077623 | 2671.01 | 0.22226 | 3117.5 | 0.24276 | 2622.53 | 0.4283 | 3131.81 | 0.38018
3083.29 | 0.051196 | 3189.93 | 0.059303 | 3892.33 | 0.058893 | 3857.46 | 0.087277 | 2419.15 | 0.2653 | 2820.3 | 0.29412 | 2372.52 | 0.51774 | 2897.22 | 0.44277
2849.07 | 0.055595 | 2906.63 | 0.066282 | 3665.65 | 0.063574 | 3578.72 | 0.097838 | 2206.14 | 0.31379 | 2570.5 | 0.34908 | 2112.21 | 0.64403 | 2649.69 | 0.52762
2648.49 | 0.060194 | 2635.28 | 0.07512 | 3459.08 | 0.068696 | 3306.87 | 0.11066 | 2001.55 | 0.37499 | 2376.6 | 0.40561 | 1864.39 | 0.81596 | 2441.41 | 0.6212
2459.57 | 0.065627 | 2415.69 | 0.084294 | 3167.68 | 0.077162 | 2998.15 | 0.12947 | 1812.82 | 0.45071 | 2223.9 | 0.46195 | 1677.03 | 1.0075 | 2220.08 | 0.74705
2300.17 | 0.070985 | 2170.55 | 0.097741 | 2857.63 | 0.089116 | 2784.29 | 0.14659 | 1636.25 | 0.5467 | 2033.89 | 0.55205 | 1534.63 | 1.2102 | 1950.65 | 0.97065
2131.82 | 0.077932 | 2003.66 | 0.10968 | 2585.68 | 0.10333 | 2534.48 | 0.17269 | 1484.51 | 0.65595 | 1832.64 | 0.67501 | 1362.35 | 1.5536 | 1741.61 | 1.2158
1989.68 | 0.084967 | 1825.71 | 0.12554 | 2309.39 | 0.12198 | 2309.39 | 0.20204 | 1322.39 | 0.80991 | 1643.76 | 0.82821 | 1229.65 | 1.9226 | 1581 | 1.4781
1805.74 | 0.096487 | 1698.88 | 0.13976 | 2081.27 | 0.14385 | 2100.08 | 0.23968 | 1198.38 | 0.97287 | 1469.29 | 1.032 | 1086 | 2.5429 | 1429.46 | 1.8365
1640.44 | 0.11022 | 1591.96 | 0.1542 | 1896.43 | 0.16696 | 1936.68 | 0.27792 | 1099.14 | 1.1573 | 1331.5 | 1.2633 | 990.949 | 3.1433 | 1316.35 | 2.1847
1471.02 | 0.12844 | 1468.09 | 0.17563 | 1719.39 | 0.19572 | 1777.08 | 0.32579 | 1000.06 | 1.3966 | 1225.44 | 1.5037 | 907.844 | 3.8655 | 1188.81 | 2.7395
1333.7 | 0.14893 | 1357.92 | 0.19945 | 1584.02 | 0.2247 | 1629 | 0.38305 | 899.566 | 1.7263 | 1104.18 | 1.8888 | 828.382 | 4.8947 | 1088.49 | 3.3478
1223.79 | 0.1693 | 1241.04 | 0.23126 | 1447.67 | 0.2621 | 1491.76 | 0.45128 | 829.806 | 2.0314 | 1018.55 | 2.2754 | 751.13 | 6.3378 | 981.352 | 4.315
1139.91 | 0.18978 | 1160.61 | 0.25977 | 1325.72 | 0.30573 | 1341.72 | 0.55265 | 753.714 | 2.5067 | 915.674 | 2.9093 | 679.135 | 8.3392 | 893.919 | 5.4638
1049.11 | 0.21659 | 1078.9 | 0.29382 | 1193.57 | 0.36886 | 1222.56 | 0.66151 | 672.943 | 3.2532 | 839.842 | 3.5615 | 622.893 | 10.9161 | 835.048 | 6.6047
957.855 | 0.25139 | 991.975 | 0.34035 | 1102.9 | 0.42644 | 1087.57 | 0.82308 | 600.827 | 4.2634 | 788.134 | 4.143 | 571.963 | 14.8655 | 773.827 | 8.2112
869.303 | 0.29616 | 912.049 | 0.39543 | 1009.99 | 0.50039 | 990.983 | 0.98913 | 543.239 | 5.5268 | 735.387 | 4.9143 | 528.212 | 20.88 | 723.278 | 10.1558
809.719 | 0.33465 | 829.389 | 0.4705 | 922.137 | 0.59068 | 903.877 | 1.1875 | 488.646 | 7.4236 | 671.02 | 6.2298 | 491.171 | 30.0077 | 673.328 | 13.0377
740.765 | 0.39074 | 767.152 | 0.54178 | 862.376 | 0.6721 | 812.152 | 1.4834 | 448.179 | 9.7567 | 619.692 | 7.7985 | 472.417 | 39.2131 | 641.715 | 15.8507
672.955 | 0.46263 | 699.72 | 0.64336 | 804.071 | 0.77085 | 742.991 | 1.788 | 424.942 | 11.7939 | 564.804 | 10.2611 | 456.727 | 54.3884 | 595.69 | 21.6474
619.352 | 0.53642 | 625.577 | 0.79181 | 748.21 | 0.88939 | 678.361 | 2.181 | 394.916 | 15.6342 | 524.896 | 13.2106 | 446.387 | 69.622 | 569.023 | 27.8539
575.748 | 0.61219 | 558.732 | 0.98619 | 697.624 | 1.0231 | 631.865 | 2.544 | 370.177 | 20.8561 | 491.171 | 16.9011 | 439.288 | 88.8676 | 542.617 | 38.3466
527.773 | 0.71836 | 510.13 | 1.1781 | 647.861 | 1.1851 | 582.699 | 3.0391 | 350.181 | 29.1269 | 464.639 | 21.2907 | 432.55 | 119.23 | 524.896 | 51.8923
492.583 | 0.81738 | 468.558 | 1.3976 | 605.875 | 1.3579 | 542.218 | 3.591 | 338.744 | 38.4346 | 443.077 | 27.2072 | 427.137 | 168.625 | 511.546 | 71.2768
458.362 | 0.93747 | 426.945 | 1.6963 | 568.88 | 1.5528 | 508.601 | 4.1846 | 326.932 | 52.8524 | 426.16 | 34.4507 | 424.942 | 241.231 | 500.538 | 100.978
420.168 | 1.1132 | 393.331 | 2.0124 | 534.679 | 1.7703 | 475.165 | 4.9397 | 320.079 | 69.2243 | 413.423 | 44.6338 | 424.942 | 339.607 | 493.991 | 134.397
384.387 | 1.3246 | 362.001 | 2.3992 | 501.029 | 2.0406 | 443.039 | 5.9127 | 313.73 | 93.0888 | 399.692 | 59.5756 | 425.185 | 421.002 | 488.087 | 199.331
349.899 | 1.5982 | 332.169 | 2.9033 | 466.688 | 2.3944 | 416.403 | 7.0213 | 308.741 | 128.009 | 387.747 | 81.223 | 424.212 | 537.071 | 486.971 | 249.954
323.643 | 1.8809 | 306.323 | 3.4995 | 442.596 | 2.6949 | 387.475 | 8.5475 | 303.831 | 186.515 | 378.752 | 114.084 | 424.455 | 596.439 | 483.914 | 330.395
306.016 | 2.1149 | 284.472 | 4.1639 | 418.909 | 3.0694 | 367.105 | 10.0497 | 301.578 | 242.617 | 371.238 | 160.794 |  |  | 483.083 | 425.366
283.336 | 2.4742 | 269.248 | 4.7662 | 398.08 | 3.4718 | 346.764 | 12.1012 | 299.685 | 334.203 | 368.064 | 205.124 |  |  | 479.776 | 527.013
260.507 | 2.9734 | 255.604 | 5.434 | 379.043 | 3.9152 | 328.535 | 14.528 | 298.316 | 440.747 | 365.126 | 272.54 |  |  | 483.637 | 601.242
239.997 | 3.5732 | 244.112 | 6.2261 | 363.452 | 4.3327 | 315.021 | 17.1325 | 298.145 | 566.788 | 362.211 | 371.358
222.655 | 4.239 | 231.742 | 7.2625 | 348.503 | 4.8329 | 302.971 | 20.0042 | 297.974 | 602.621 | 360.762 | 464.602
208.433 | 5.0139 | 221.323 | 8.4127 | 333.834 | 5.4394 | 289.06 | 25.3142 |  |  | 359.114 | 559.689
195.12 | 5.9068 | 212.219 | 9.7064 | 321.064 | 6.0734 | 277.171 | 31.4661 |  |  | 359.32 | 601.586
184.678 | 6.8491 | 203.287 | 11.2547 | 304.49 | 7.0353 | 267.637 | 38.2295
174.445 | 8.0051 | 195.511 | 13.0242 | 293.136 | 7.832 | 259.727 | 46.5852
168.276 | 8.8763 | 188.786 | 15.0719 | 282.205 | 8.7885 | 251.295 | 58.7173
162.164 | 9.8913 | 182.11 | 17.6683 | 272.226 | 9.9702 | 243.624 | 76.1718
157.056 | 11.0114 | 175.846 | 20.8357 | 261.29 | 11.5034 | 236.66 | 100
151.2 | 12.8189 | 170.478 | 24.5709 | 250.543 | 13.3916 | 231.51 | 128.699
146.584 | 14.6877 | 166.602 | 28.4341 | 243.137 | 15.057 | 227.153 | 166.295
140.134 | 17.9871 | 162.326 | 34.4088 | 236.897 | 17.0138 | 223.771 | 214.873
136.264 | 20.6298 | 159.59 | 40.2561 | 229.666 | 19.6497 | 220.219 | 284.058
131.841 | 24.5222 | 157.056 | 47.4728 | 223.547 | 22.6264 | 216.723 | 386.879
128.2 | 28.947 | 154.254 | 57.334 | 217.81 | 26.288 | 214.781 | 502.383
125.16 | 34.1025 | 151.958 | 69.2436 | 213.07 | 30.3004 | 214.352 | 600.146
122.559 | 40.1363 | 150.295 | 82.8004 | 208.642 | 35.0295
120.372 | 47.0503 | 148.502 | 104.26 | 204.306 | 40.901
118.107 | 57.5622 | 146.584 | 130.761 | 200.26 | 47.7092
116.465 | 68.8321 | 144.836 | 182.027 | 196.687 | 56.8802
114.731 | 82.0635 | 142.965 | 254.15 | 193.372 | 67.8815
113.136 | 100 | 141.826 | 339.335 | 190.112 | 81.1717
111.898 | 126.796 | 140.836 | 471.907 | 186.721 | 100
110.895 | 172.349 | 140.274 | 584.844 | 183.941 | 121.012
110.342 | 220.276 | 140.134 | 600.146 | 181.202 | 154.509
109.682 | 279.857 |  |  | 179.04 | 188.655
109.135 | 342.043 |  |  | 176.375 | 239.445
108.699 | 445.487 |  |  | 174.794 | 290.334
108.591 | 573.91 |  |  | 172.537 | 391.518
108.591 | 600.146 |  |  | 171.333 | 540.166
|  |  |  | 170.991 | 600.146