## 165_22
S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (7.2 and 14.4 kV)
"K" Speed (TCC 165-2-2) | [9 empty] | "K" Speed (TCC 165-2-2) | [9 empty] | "K" Speed (TCC 165-2-2) | [9 empty] | "K" Speed (TCC 165-2-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3K |  | 6K |  | 8K |  | 10K |  | 12K |  | 15K |  | 20K |  | 25K |  | 30K |  | 40K |  | 50K |  | 65K |  | 80K |  | 100K |  | 140K |  | 200K
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
17960.4 | 0.015968 | 17960.4 | 0.015968 | 17960.4 | 0.015968 | 17960.4 | 0.015968 | 17960.4 | 0.015968 | 17960.4 | 0.015968 | 17960.4 | 0.016145 | 17960.4 | 0.016145 | 17960.4 | 0.016145 | 17960.4 | 0.016145 | 17960.4 | 0.016145 | 17960.4 | 0.016307 | 17960.4 | 0.016307 | 17960.4 | 0.016307 | 17960.4 | 0.017229 | 17960.4 | 0.026859
5895.4 | 0.018682 | 3391.16 | 0.020057 | 5425.84 | 0.018833 | 5028.76 | 0.019877 | 4889.91 | 0.019917 | 6038.6 | 0.019406 | 6620.51 | 0.020117 | 5239.22 | 0.021771 | 7179.09 | 0.019977 | 8901.08 | 0.019562 | 10828.4 | 0.018889 | 13318.7 | 0.018221 | 12938 | 0.018552 | 13973.6 | 0.018294 | 16662.6 | 0.017789 | 17170.1 | 0.027649
2286.84 | 0.021234 | 1377.36 | 0.022614 | 1919.71 | 0.021749 | 3515.47 | 0.021022 | 2416.14 | 0.022367 | 4656.08 | 0.020689 | 4527.51 | 0.022167 | 4150.27 | 0.02342 | 5709.74 | 0.021404 | 7676.57 | 0.020544 | 8981.55 | 0.020299 | 11636.8 | 0.019309 | 10785.1 | 0.020158 | 11036.1 | 0.020462 | 15198.1 | 0.018664 | 16073.5 | 0.028922
1240.07 | 0.022933 | 1044.12 | 0.023561 | 1640.78 | 0.022345 | 2203.78 | 0.02266 | 1919.71 | 0.023514 | 3597.26 | 0.022056 | 3823.53 | 0.023141 | 3515.47 | 0.024794 | 4797.87 | 0.022637 | 6876.93 | 0.021276 | 7287.59 | 0.022034 | 10290 | 0.020442 | 8672.64 | 0.022322 | 9329.42 | 0.022322 | 13959.6 | 0.019601 | 14986.8 | 0.030283
1045.16 | 0.02349 | 894.201 | 0.02423 | 1280.4 | 0.023467 | 1699.23 | 0.023774 | 1724.91 | 0.024206 | 2892.65 | 0.02321 | 3165.06 | 0.024206 | 3139.84 | 0.025625 | 4092.57 | 0.023893 | 5996.48 | 0.022367 | 6105.4 | 0.023608 | 8552.06 | 0.022322 | 7539.63 | 0.024109 | 8224.95 | 0.023941 | 12732.6 | 0.020938 | 14213.2 | 0.031582
854 | 0.024278 | 784.409 | 0.025194 | 1067.34 | 0.024522 | 1504.07 | 0.024278 | 1540.6 | 0.024868 | 2307.52 | 0.024303 | 2959.95 | 0.02467 | 2809.97 | 0.026618 | 3611.68 | 0.024918 | 5302.47 | 0.02335 | 4953.89 | 0.02578 | 7390.33 | 0.023917 | 6640.4 | 0.026065 | 7302.18 | 0.025805 | 11636.8 | 0.022412 | 13358.7 | 0.033168
758.188 | 0.024893 | 710.473 | 0.026091 | 926.979 | 0.025523 | 1285.53 | 0.025244 | 1333.99 | 0.025987 | 2081.67 | 0.024893 | 2689.01 | 0.02532 | 2557.86 | 0.027621 | 3235.47 | 0.025961 | 4582.17 | 0.024621 | 4272.39 | 0.027566 | 6502.41 | 0.0256 | 5854.28 | 0.028377 | 6633.77 | 0.027732 | 10435 | 0.024376 | 12418.3 | 0.035466
700.596 | 0.025295 | 647.378 | 0.026939 | 825.452 | 0.026565 | 1083.47 | 0.026432 | 1189.07 | 0.026886 | 1879.81 | 0.025549 | 2404.09 | 0.02638 | 2319.09 | 0.028605 | 2915.88 | 0.027183 | 3971.62 | 0.026143 | 3586.49 | 0.030072 | 5624.73 | 0.027566 | 5084.38 | 0.03133 | 5871.87 | 0.030435 | 9546.48 | 0.026459 | 11440.6 | 0.038267
661.779 | 0.025651 | 570.738 | 0.028123 | 726.277 | 0.027788 | 960.958 | 0.027511 | 1056.72 | 0.028067 | 1667.24 | 0.026512 | 2119.48 | 0.027539 | 2104.7 | 0.029892 | 2573.26 | 0.028749 | 3470.06 | 0.027732 | 3077.67 | 0.032414 | 4688.78 | 0.030649 | 4389.31 | 0.035114 | 5187.09 | 0.033737 | 8534.98 | 0.029594 | 10656.5 | 0.041083
609.678 | 0.026327 | 498.663 | 0.029654 | 630.133 | 0.029359 | 859.139 | 0.028662 | 947.598 | 0.029212 | 1498.06 | 0.027429 | 1822.43 | 0.029067 | 1851.83 | 0.031487 | 2347.08 | 0.030012 | 3022.77 | 0.029594 | 2596.52 | 0.035751 | 4080.31 | 0.033368 | 3796.85 | 0.039709 | 4541.12 | 0.038038 | 7738.23 | 0.032642 | 9827.38 | 0.044907
552.764 | 0.027047 | 446.273 | 0.030864 | 545.079 | 0.031112 | 765.042 | 0.029922 | 855.709 | 0.030404 | 1358.22 | 0.028491 | 1582.76 | 0.03071 | 1662.25 | 0.033102 | 2119.48 | 0.031362 | 2702.49 | 0.031237 | 2252.8 | 0.039157 | 3497.94 | 0.037099 | 3235.47 | 0.045585 | 3924.24 | 0.043492 | 6911.4 | 0.037062 | 9153.83 | 0.048989
497.17 | 0.027927 | 396.601 | 0.032382 | 483.442 | 0.032707 | 669.768 | 0.03174 | 778.159 | 0.031772 | 1222.83 | 0.029683 | 1408 | 0.032382 | 1510.09 | 0.034834 | 1958.49 | 0.032642 | 2399.29 | 0.033168 | 2002.05 | 0.042334 | 3040.96 | 0.041083 | 2815.59 | 0.052122 | 3466.6 | 0.049283 | 6253.7 | 0.041454 | 8233.18 | 0.055401
448.51 | 0.028922 | 328.958 | 0.035325 | 422.391 | 0.035149 | 590.477 | 0.033737 | 704.812 | 0.033334 | 1091.08 | 0.031205 | 1232.66 | 0.034522 | 1374.61 | 0.036693 | 1781 | 0.034418 | 2058.9 | 0.036474 | 1800.69 | 0.045998 | 2654.28 | 0.045722 | 2447.76 | 0.060497 | 3093.1 | 0.055901 | 5535.45 | 0.048067 | 7442.25 | 0.063029
403.401 | 0.029952 | 292.636 | 0.037697 | 379.529 | 0.037472 | 518.495 | 0.036547 | 646.731 | 0.034904 | 958.08 | 0.033201 | 1100.95 | 0.036767 | 1250.04 | 0.03869 | 1616.35 | 0.036255 | 1846.28 | 0.039236 | 1663.91 | 0.04958 | 2335.38 | 0.051346 | 2157.98 | 0.069867 | 2746.08 | 0.064302 | 5043.87 | 0.053871 | 6660.36 | 0.072864
366.475 | 0.030864 | 256.706 | 0.040512 | 331.932 | 0.040674 | 462.169 | 0.03963 | 585.187 | 0.037062 | 857.423 | 0.03536 | 994.192 | 0.038962 | 1134.48 | 0.041001 | 1432.14 | 0.03904 | 1678.96 | 0.041829 | 1513.12 | 0.054304 | 2058.9 | 0.058183 | 1806.1 | 0.087059 | 2484.75 | 0.072864 | 4411.32 | 0.064302 | 5790.24 | 0.088818
339.655 | 0.03174 | 227.45 | 0.043798 | 290.015 | 0.045042 | 408.679 | 0.043449 | 534.286 | 0.039393 | 747.647 | 0.038459 | 894.201 | 0.041704 | 1022.42 | 0.043974 | 1301.05 | 0.041537 | 1552.97 | 0.044638 | 1369.13 | 0.061166 | 1770.34 | 0.068346 | 1552.97 | 0.10665 | 2237.08 | 0.084402 | 3916.4 | 0.075761 | 5291.88 | 0.10155
309.801 | 0.03297 | 199.324 | 0.048259 | 262.679 | 0.049087 | 366.842 | 0.047731 | 479.59 | 0.042546 | 662.441 | 0.041413 | 814.79 | 0.044594 | 934.424 | 0.046927 | 1192.64 | 0.044282 | 1433.58 | 0.047875 | 1256.3 | 0.067599 | 1535.99 | 0.080446 | 1350.09 | 0.12975 | 1998.05 | 0.098651 | 3401.35 | 0.093092 | 4745.39 | 0.11918
287.129 | 0.034008 | 180.356 | 0.052331 | 229.966 | 0.055511 | 331.269 | 0.052018 | 437.436 | 0.04609 | 598.204 | 0.044594 | 740.948 | 0.047875 | 863.446 | 0.050128 | 1001.17 | 0.051192 | 1335.32 | 0.051192 | 1178.42 | 0.07367 | 1301.05 | 0.098849 | 1199.82 | 0.15565 | 1761.51 | 0.11929 | 2995.69 | 0.11291 | 4341.3 | 0.13777
262.416 | 0.035431 | 165.163 | 0.05652 | 204.165 | 0.063281 | 297.356 | 0.057431 | 396.601 | 0.050632 | 540.736 | 0.048598 | 675.147 | 0.051759 | 777.381 | 0.054358 | 902.285 | 0.056069 | 1241.32 | 0.054959 | 1091.08 | 0.082813 | 1137.89 | 0.11834 | 1048.3 | 0.19317 | 1504.07 | 0.15302 | 2664.92 | 0.13599 | 3889.08 | 0.16445
243.211 | 0.036877 | 147.368 | 0.062777 | 183.999 | 0.071421 | 270.678 | 0.063471 | 358.86 | 0.055623 | 485.38 | 0.053335 | 624.487 | 0.055401 | 716.18 | 0.058768 | 789.919 | 0.064302 | 1091.08 | 0.063535 | 1000.17 | 0.09431 | 996.183 | 0.14527 | 938.17 | 0.23524 | 1293.27 | 0.19688 | 2323.73 | 0.17014 | 3452.76 | 0.19986
222.946 | 0.03869 | 131.096 | 0.07071 | 162.379 | 0.083646 | 244.43 | 0.071065 | 331.932 | 0.060618 | 433.951 | 0.059715 | 571.881 | 0.060922 | 662.441 | 0.064045 | 712.608 | 0.072139 | 988.245 | 0.071207 | 915.922 | 0.10892 | 855.709 | 0.18579 | 809.107 | 0.306 | 1169.03 | 0.23406 | 2077.52 | 0.20533 | 3165.06 | 0.2322
203.961 | 0.040633 | 116.738 | 0.080527 | 143.585 | 0.098553 | 218.095 | 0.081989 | 307.026 | 0.066592 | 393.441 | 0.066326 | 523.706 | 0.066859 | 604.216 | 0.070569 | 646.085 | 0.082071 | 898.683 | 0.081011 | 822.979 | 0.12884 | 744.662 | 0.23547 | 691.547 | 0.4065 | 1046.21 | 0.28446 | 1813.34 | 0.26206 | 2878.22 | 0.27331
164.998 | 0.046274 | 105.84 | 0.089353 | 126.208 | 0.11787 | 195.572 | 0.094216 | 284.272 | 0.073302 | 362.104 | 0.073596 | 483.926 | 0.07367 | 541.277 | 0.081174 | 586.358 | 0.09384 | 824.627 | 0.090431 | 696.405 | 0.16811 | 628.874 | 0.31595 | 582.851 | 0.5643 | 929.764 | 0.35163 | 1630.97 | 0.31785 | 2664.92 | 0.31532
149.296 | 0.049432 | 94.5316 | 0.1034 | 110.27 | 0.14614 | 173.111 | 0.11145 | 257.477 | 0.083981 | 320.516 | 0.085849 | 450.758 | 0.080688 | 490.748 | 0.092443 | 515.909 | 0.11404 | 737.991 | 0.10623 | 602.406 | 0.21349 | 536.427 | 0.42183 | 509.755 | 0.74441 | 832.082 | 0.43424 | 1472.81 | 0.38552 | 2477.31 | 0.36307
133.344 | 0.053335 | 82.0997 | 0.12591 | 95.5771 | 0.18412 | 152.008 | 0.13477 | 231.35 | 0.097767 | 287.129 | 0.099842 | 405.829 | 0.092721 | 427.49 | 0.11336 | 459.864 | 0.13846 | 667.094 | 0.12268 | 531.621 | 0.26311 | 455.288 | 0.57801 | 446.273 | 0.99088 | 756.673 | 0.52458 | 1343.36 | 0.46526 | 2316.77 | 0.41763
121.017 | 0.057317 | 74.3612 | 0.14644 | 79.9126 | 0.24904 | 130.182 | 0.17184 | 206.63 | 0.11565 | 257.477 | 0.11635 | 367.576 | 0.10762 | 373.879 | 0.14055 | 398.191 | 0.17602 | 603.612 | 0.14397 | 451.209 | 0.35304 | 393.441 | 0.7865 | 396.601 | 1.2915 | 673.798 | 0.66954 | 1208.25 | 0.57801 | 2168.8 | 0.47943
111.489 | 0.061596 | 66.0845 | 0.17655 | 71.7318 | 0.30235 | 111.044 | 0.22198 | 178.561 | 0.14614 | 234.611 | 0.13477 | 326.011 | 0.12962 | 307.64 | 0.19668 | 354.579 | 0.21585 | 557.761 | 0.1633 | 392.655 | 0.45971 | 341.699 | 1.0842 | 363.555 | 1.5949 | 607.244 | 0.83848 | 1117.59 | 0.68649 | 2006.06 | 0.5677
101.385 | 0.066993 | 59.8555 | 0.20843 | 60.6387 | 0.4065 | 94.4371 | 0.29224 | 158.528 | 0.17743 | 207.458 | 0.16249 | 295.873 | 0.1506 | 263.731 | 0.25765 | 301.247 | 0.28934 | 486.351 | 0.20615 | 345.479 | 0.59146 | 300.946 | 1.4591 | 337.623 | 1.9481 | 572.453 | 0.95872 | 1013.26 | 0.85286 | 1870.44 | 0.66821
93.591 | 0.071923 | 54.54 | 0.24656 | 52.2445 | 0.53357 | 78.9594 | 0.40085 | 134.819 | 0.23524 | 184.737 | 0.19846 | 257.477 | 0.18822 | 217.224 | 0.36672 | 258.251 | 0.38823 | 441.391 | 0.24435 | 308.256 | 0.75945 | 272.852 | 1.8586 | 318.917 | 2.2792 | 534.286 | 1.1307 | 925.127 | 1.0532 | 1747.48 | 0.78336
85.6213 | 0.079011 | 49.0546 | 0.29845 | 43.3772 | 0.7717 | 65.1006 | 0.56827 | 117.206 | 0.30145 | 164.998 | 0.24143 | 234.143 | 0.22176 | 178.383 | 0.53091 | 206.424 | 0.5986 | 384.111 | 0.31817 | 268.253 | 1.0543 | 255.937 | 2.1921 | 307.333 | 2.5621 | 486.351 | 1.4231 | 852.293 | 1.2877 | 1613.12 | 0.95393
77.7839 | 0.087846 | 42.2217 | 0.39567 | 40.2832 | 0.91014 | 56.6524 | 0.7459 | 103.33 | 0.37864 | 138.508 | 0.32885 | 203.758 | 0.28219 | 147.073 | 0.78024 | 178.919 | 0.80803 | 342.383 | 0.39845 | 236.733 | 1.4132 | 246.64 | 2.4299 | 293.809 | 2.9827 | 453.018 | 1.697 | 793.879 | 1.5665 | 1468.4 | 1.2212
72.3079 | 0.095927 | 36.9636 | 0.5147 | 37.5222 | 1.067 | 53.034 | 0.85628 | 91.1889 | 0.48087 | 118.147 | 0.43948 | 179.995 | 0.35128 | 122.6 | 1.1547 | 159.482 | 1.0396 | 305.189 | 0.49999 | 210.804 | 1.9133 | 235.081 | 2.77 | 280.881 | 3.4447 | 424.933 | 2.0195 | 739.468 | 1.9578 | 1337.99 | 1.5712
66.7486 | 0.10655 | 33.1796 | 0.64716 | 35.6566 | 1.2175 | 48.9077 | 1.018 | 80.0726 | 0.61806 | 101.792 | 0.58792 | 160.924 | 0.43164 | 115.115 | 1.3349 | 149.894 | 1.1982 | 273.672 | 0.63055 | 197.736 | 2.2566 | 222.056 | 3.363 | 266.915 | 4.1655 | 403.401 | 2.3183 | 699.196 | 2.3323 | 1243.8 | 1.9325
60.8818 | 0.12061 | 29.8425 | 0.81208 | 33.2792 | 1.4694 | 44.6089 | 1.2622 | 72.1635 | 0.76479 | 88.1406 | 0.78887 | 138.924 | 0.57169 | 109.282 | 1.5202 | 141.873 | 1.3852 | 238.634 | 0.84269 | 190.363 | 2.5265 | 213.349 | 3.8684 | 254.66 | 5.0523 | 388.359 | 2.5905 | 663.767 | 2.7534 | 1165.52 | 2.351
54.54 | 0.14112 | 26.0739 | 1.1239 | 31.6562 | 1.6936 | 41.1381 | 1.5494 | 67.2848 | 0.89122 | 78.7229 | 0.99684 | 123.215 | 0.73333 | 103.848 | 1.7382 | 134.549 | 1.5902 | 214.419 | 1.0713 | 182.35 | 2.9004 | 204.984 | 4.5669 | 242.968 | 6.3461 | 372.759 | 2.959 | 631.395 | 3.3063 | 1103.15 | 2.8118
46.1979 | 0.18211 | 23.8297 | 1.4203 | 29.7531 | 2.0316 | 38.1274 | 1.8829 | 62.7359 | 1.0438 | 72.8887 | 1.191 | 109.501 | 0.93973 | 99.3783 | 1.9874 | 127.222 | 1.8905 | 196.946 | 1.2967 | 174.327 | 3.3462 | 196.749 | 5.5281 | 234.611 | 7.7822 | 355.644 | 3.4104 | 602.406 | 3.9862 | 1032.69 | 3.5817
41.1381 | 0.22043 | 21.866 | 1.8273 | 27.825 | 2.4964 | 35.8712 | 2.2207 | 58.4946 | 1.2335 | 66.6153 | 1.4976 | 101.183 | 1.115 | 95.1004 | 2.2543 | 120.654 | 2.1855 | 181.079 | 1.5791 | 165.163 | 4.1531 | 187.528 | 7.0911 | 226.542 | 9.7947 | 339.655 | 4.0586 | 575.323 | 4.8203 | 987.257 | 4.2667
36.051 | 0.27771 | 20.3674 | 2.3369 | 26.1522 | 3.0339 | 33.8498 | 2.6113 | 53.9973 | 1.5051 | 61.3708 | 1.8698 | 94.6261 | 1.3071 | 93.0311 | 2.4347 | 116.155 | 2.5089 | 167.157 | 1.952 | 159.322 | 4.8251 | 181.079 | 8.8449 | 220.287 | 12.1441 | 324.061 | 4.8981 | 547.264 | 6.0973 | 948.546 | 5.2375
30.7514 | 0.37152 | 19.4906 | 2.707 | 24.58 | 3.6504 | 32.2957 | 3.043 | 49.9956 | 1.8127 | 55.6418 | 2.4567 | 88.7598 | 1.5401 | 89.2047 | 2.7617 | 109.282 | 3.1045 | 155.389 | 2.4009 | 152.922 | 5.9112 | 175.903 | 11.2666 | 213.563 | 15.2998 | 307.948 | 6.0851 | 526.858 | 7.3364 | 911.353 | 6.4099
27.1651 | 0.47182 | 18.5401 | 3.3362 | 23.0562 | 4.5533 | 30.7514 | 3.6213 | 46.6155 | 2.1811 | 52.7168 | 2.8946 | 82.8419 | 1.8717 | 85.2795 | 3.1831 | 103.124 | 3.807 | 149.147 | 2.6935 | 147.663 | 7.3071 | 170.363 | 14.4666 | 208.082 | 19.3336 | 294.692 | 7.5071 | 508.737 | 8.916 | 880.008 | 7.7589
23.8059 | 0.61745 | 17.3733 | 4.4408 | 21.9537 | 5.5669 | 29.3395 | 4.3879 | 44.2978 | 2.4964 | 50.5991 | 3.313 | 77.1641 | 2.3045 | 81.8537 | 3.7279 | 98.0947 | 4.6221 | 139.342 | 3.28 | 142.157 | 9.5338 | 165.825 | 18.7998 | 203.758 | 25.2252 | 285.126 | 9.3357 | 491.731 | 11.0435 | 845.502 | 10.2558
21.1139 | 0.79839 | 16.4765 | 5.7537 | 20.9457 | 6.8267 | 28.1046 | 5.2375 | 42.5608 | 2.8118 | 48.9077 | 3.7428 | 71.1602 | 3.0097 | 78.6442 | 4.4099 | 94.9104 | 5.4349 | 133.21 | 3.7729 | 137.955 | 12.5014 | 162.054 | 24.4308 | 197.933 | 37.22 | 274.22 | 12.2049 | 468.217 | 15.6089 | 819.694 | 12.9986
18.7451 | 1.0406 | 15.8146 | 7.1338 | 20.2455 | 8.2635 | 26.8411 | 6.6183 | 40.892 | 3.2183 | 47.1311 | 4.3835 | 67.4869 | 3.571 | 75.9393 | 5.2585 | 92.1976 | 6.3145 | 127.094 | 4.4143 | 133.744 | 16.7575 | 159.163 | 32.1639 | 194.792 | 48.8057 | 263.468 | 16.2948 | 453.471 | 19.7044 | 782.06 | 18.7434
16.5922 | 1.37 | 15.3779 | 8.6611 | 19.5687 | 10.4734 | 25.532 | 8.5749 | 39.4461 | 3.6541 | 44.3864 | 5.771 | 63.7478 | 4.4231 | 73.4742 | 6.2893 | 89.4727 | 7.7357 | 121.745 | 5.1184 | 130.703 | 22.5525 | 155.7 | 45.6429 | 190.744 | 75.0271 | 257.735 | 20.0423 | 431.786 | 29.6614 | 747.647 | 27.3809
13.9703 | 2.0582 | 15.0584 | 10.3796 | 19.1621 | 12.7667 | 24.6539 | 10.547 | 37.8994 | 4.3225 | 42.6034 | 7.1481 | 61.4322 | 5.2585 | 70.9471 | 7.7202 | 87.5258 | 9.1875 | 117.675 | 5.8465 | 127.859 | 34.9824 | 153.535 | 61.7348 | 188.468 | 103.736 | 251.623 | 25.8121 | 419.025 | 39.2067 | 719.05 | 40.4411
12.1939 | 2.8629 | 14.7602 | 13.5156 | 18.8014 | 17.0448 | 23.9971 | 12.703 | 36.2679 | 5.2954 | 41.0559 | 9.2243 | 58.8466 | 6.559 | 68.9881 | 9.6296 | 85.6213 | 10.9445 | 113.514 | 7.0136 | 125.453 | 56.2524 | 151.401 | 85.5285 | 186.034 | 146.181 | 245.165 | 35.3694 | 405.829 | 55.5814 | 699.196 | 56.4778
11.1221 | 3.5997 | 14.6426 | 16.7742 | 18.6516 | 22.7336 | 23.5219 | 15.6715 | 34.6721 | 6.6316 | 39.5646 | 12.0353 | 56.3698 | 8.5151 | 66.4157 | 13.5969 | 83.4238 | 13.9551 | 109.173 | 8.4388 | 123.832 | 95.4736 | 150.345 | 123.205 | 184.737 | 216.99 | 238.395 | 53.8848 | 395.413 | 77.933 | 680.57 | 81.6833
10.548 | 4.1697 | 14.5987 | 24.2847 | 18.633 | 35.6891 | 23.2646 | 19.1987 | 33.3125 | 8.3132 | 38.5106 | 15.2235 | 54.1595 | 11.0214 | 64.1956 | 20.3452 | 81.8537 | 18.1169 | 106.584 | 9.8242 | 122.6 | 197.127 | 149.147 | 183.616 | 183.631 | 312.265 | 232.742 | 98.6768 | 386.036 | 110.702 | 660.456 | 119.205
10.0939 | 4.6592 | 14.5841 | 39.839 | 18.5586 | 58.4896 | 22.9641 | 25.7091 | 32.1025 | 10.685 | 37.8615 | 19.0648 | 52.5063 | 14.3944 | 62.7359 | 28.958 | 80.474 | 22.9391 | 104.16 | 11.5634 | 121.259 | 345.451 | 147.81 | 287.681 | 182.35 | 457.992 | 229.506 | 163.342 | 376.505 | 158.356 | 642.863 | 168.485
9.7079 | 5.3808 | 14.5841 | 76.8495 | 18.5401 | 99.868 | 22.8954 | 37.707 | 31.1537 | 13.7748 | 37.3725 | 25.2252 | 51.1588 | 19.1221 | 61.8637 | 43.1571 | 79.2759 | 29.6614 | 101.487 | 14.1518 | 120.654 | 543.948 | 146.779 | 424.05 | 181.804 | 562.76 | 226.769 | 268.232 | 367.944 | 225.394 | 628.246 | 231.563
9.3366 | 6.1894 | 14.5695 | 140.169 | 18.4291 | 176.24 | 22.8954 | 60.7549 | 30.5063 | 18.135 | 37.0747 | 36.5926 | 50.0956 | 26.8656 | 61.3708 | 71.083 | 78.3302 | 41.7562 | 99.5772 | 16.8583 | 120.293 | 605.378 | 145.901 | 549.414 | 180.898 | 601.757 | 225.864 | 390.666 | 362.104 | 316.667 | 613.347 | 315.403
8.8901 | 7.7745 | 14.5114 | 245.882 | 18.3923 | 292.613 | 22.8954 | 128.489 | 30.1123 | 23.5434 | 37.0747 | 65.095 | 49.2512 | 46.7516 | 60.8818 | 129.004 | 77.3185 | 60.5124 | 97.3131 | 20.9858 |  |  | 145.174 | 605.984 |  |  | 224.512 | 542.861 | 357.427 | 420.671 | 598.204 | 423.203
8.6015 | 9.4957 | 14.5114 | 431.321 | 18.3189 | 467.712 | 22.8268 | 247.609 | 30.0822 | 32.8465 | 37.0747 | 118.019 | 48.9077 | 78.1671 | 60.5176 | 240.051 | 76.7792 | 90.5452 | 95.3862 | 25.9675 | [6 empty] | 222.723 | 602.961 | 353.164 | 558.276 | 587.532 | 539.074
8.3891 | 11.2441 | 14.5114 | 543.948 | 18.264 | 562.197 | 22.804 | 453.889 | 30.0822 | 52.6069 | 37.0747 | 222.483 | 48.6151 | 139.749 | 60.2158 | 409.056 | 76.1674 | 137.393 | 93.9661 | 32.2929 | [8 empty] | 352.106 | 605.378 | 579.364 | 602.359
8.1249 | 14.3801 | 14.4246 | 605.984 | 18.264 | 607.197 | 22.7812 | 566.147 | 30.0822 | 104.047 | 37.0006 | 381.02 | 48.3243 | 270.657 | 59.8555 | 550.514 | 75.7118 | 204.149 | 92.6597 | 42.3449
7.9481 | 18.0988 |  |  |  |  | 22.6902 | 607.197 | 30.0822 | 203.741 | 37.0006 | 551.065 | 47.8913 | 451.174 | 59.6166 | 613.299 | 74.9584 | 332.238 | 91.3715 | 59.7906
7.7519 | 24.0912 | [6 empty] | 30.0822 | 378.362 | 36.8529 | 609.021 | 47.7001 | 558.276 |  |  | 74.3612 | 493.663 | 90.7341 | 91.9136
7.5832 | 32.0997 | [6 empty] | 30.0822 | 543.948 |  |  | 47.6048 | 607.805 |  |  | 73.9903 | 573.555 | 90.3719 | 131.348
7.4629 | 45.5972 | [6 empty] | 30.0822 | 604.773 | [6 empty] | 73.9903 | 611.462 | 89.8313 | 196.93
7.3665 | 73.1015 | [16 empty] | 89.4727 | 280.017
7.2786 | 125.568 | [16 empty] | 89.0265 | 402.563
7.2206 | 227.659 | [16 empty] | 88.7598 | 526.817
7.2206 | 351.374 | [16 empty] | 88.6711 | 602.961
7.2206 | 506.16
7.2206 | 605.378