## 692-9-C2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Very Inverse I.E.C. (C2) (TCC 692-9-C2) | [9 empty] | Very Inverse I.E.C. (C2) (TCC 692-9-C2) | [9 empty] | Very Inverse I.E.C. (C2) (TCC 692-9-C2)
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.05 |  | Time Dial = 0.1 |  | Time Dial = 0.2 |  | Time Dial = 0.3 |  | Time Dial = 0.4 |  | Time Dial = 0.5 |  | Time Dial = 0.6 |  | Time Dial = 0.7 |  | Time Dial = 0.8 |  | Time Dial = 0.9 |  | Time Dial = 1.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 1.35 | 1.5 | 2.7 | 1.5 | 5.4 | 1.5 | 8.1 | 1.5 | 10.8 | 1.5 | 13.5 | 1.5 | 16.2 | 1.5 | 18.9 | 1.5 | 21.6 | 1.5 | 24.3 | 1.5 | 27
1.6 | 1.125 | 1.6 | 2.25 | 1.6 | 4.5 | 1.6 | 6.75 | 1.6 | 9 | 1.6 | 11.25 | 1.6 | 13.5 | 1.6 | 15.75 | 1.6 | 18 | 1.6 | 20.25 | 1.6 | 22.5
1.7 | 0.96429 | 1.7 | 1.9286 | 1.7 | 3.8571 | 1.7 | 5.7857 | 1.7 | 7.7143 | 1.7 | 9.6429 | 1.7 | 11.5714 | 1.7 | 13.5 | 1.7 | 15.4286 | 1.7 | 17.3571 | 1.7 | 19.2857
1.8 | 0.84375 | 1.8 | 1.6875 | 1.8 | 3.375 | 1.8 | 5.0625 | 1.8 | 6.75 | 1.8 | 8.4375 | 1.8 | 10.125 | 1.8 | 11.8125 | 1.8 | 13.5 | 1.8 | 15.1875 | 1.8 | 16.875
1.9 | 0.75 | 1.9 | 1.5 | 1.9 | 3 | 1.9 | 4.5 | 1.9 | 6 | 1.9 | 7.5 | 1.9 | 9 | 1.9 | 10.5 | 1.9 | 12 | 1.9 | 13.5 | 1.9 | 15
2 | 0.675 | 2 | 1.35 | 2 | 2.7 | 2 | 4.05 | 2 | 5.4 | 2 | 6.75 | 2 | 8.1 | 2 | 9.45 | 2 | 10.8 | 2 | 12.15 | 2 | 13.5
2.1 | 0.61364 | 2.1 | 1.2273 | 2.1 | 2.4545 | 2.1 | 3.6818 | 2.1 | 4.9091 | 2.1 | 6.1364 | 2.1 | 7.3636 | 2.1 | 8.5909 | 2.1 | 9.8182 | 2.1 | 11.0455 | 2.1 | 12.2727
2.2 | 0.5625 | 2.2 | 1.125 | 2.2 | 2.25 | 2.2 | 3.375 | 2.2 | 4.5 | 2.2 | 5.625 | 2.2 | 6.75 | 2.2 | 7.875 | 2.2 | 9 | 2.2 | 10.125 | 2.2 | 11.25
2.3 | 0.51923 | 2.3 | 1.0385 | 2.3 | 2.0769 | 2.3 | 3.1154 | 2.3 | 4.1538 | 2.3 | 5.1923 | 2.3 | 6.2308 | 2.3 | 7.2692 | 2.3 | 8.3077 | 2.3 | 9.3462 | 2.3 | 10.3846
2.4 | 0.48214 | 2.4 | 0.96429 | 2.4 | 1.9286 | 2.4 | 2.8929 | 2.4 | 3.8571 | 2.4 | 4.8214 | 2.4 | 5.7857 | 2.4 | 6.75 | 2.4 | 7.7143 | 2.4 | 8.6786 | 2.4 | 9.6429
2.5 | 0.45 | 2.5 | 0.9 | 2.5 | 1.8 | 2.5 | 2.7 | 2.5 | 3.6 | 2.5 | 4.5 | 2.5 | 5.4 | 2.5 | 6.3 | 2.5 | 7.2 | 2.5 | 8.1 | 2.5 | 9
2.6 | 0.42188 | 2.6 | 0.84375 | 2.6 | 1.6875 | 2.6 | 2.5312 | 2.6 | 3.375 | 2.6 | 4.2188 | 2.6 | 5.0625 | 2.6 | 5.9062 | 2.6 | 6.75 | 2.6 | 7.5938 | 2.6 | 8.4375
2.7 | 0.39706 | 2.7 | 0.79412 | 2.7 | 1.5882 | 2.7 | 2.3824 | 2.7 | 3.1765 | 2.7 | 3.9706 | 2.7 | 4.7647 | 2.7 | 5.5588 | 2.7 | 6.3529 | 2.7 | 7.1471 | 2.7 | 7.9412
2.8 | 0.375 | 2.8 | 0.75 | 2.8 | 1.5 | 2.8 | 2.25 | 2.8 | 3 | 2.8 | 3.75 | 2.8 | 4.5 | 2.8 | 5.25 | 2.8 | 6 | 2.8 | 6.75 | 2.8 | 7.5
2.9 | 0.35526 | 2.9 | 0.71053 | 2.9 | 1.4211 | 2.9 | 2.1316 | 2.9 | 2.8421 | 2.9 | 3.5526 | 2.9 | 4.2632 | 2.9 | 4.9737 | 2.9 | 5.6842 | 2.9 | 6.3947 | 2.9 | 7.1053
3 | 0.3375 | 3 | 0.675 | 3 | 1.35 | 3 | 2.025 | 3 | 2.7 | 3 | 3.375 | 3 | 4.05 | 3 | 4.725 | 3 | 5.4 | 3 | 6.075 | 3 | 6.75
3.1 | 0.32143 | 3.1 | 0.64286 | 3.1 | 1.2857 | 3.1 | 1.9286 | 3.1 | 2.5714 | 3.1 | 3.2143 | 3.1 | 3.8571 | 3.1 | 4.5 | 3.1 | 5.1429 | 3.1 | 5.7857 | 3.1 | 6.4286
3.2 | 0.30682 | 3.2 | 0.61364 | 3.2 | 1.2273 | 3.2 | 1.8409 | 3.2 | 2.4545 | 3.2 | 3.0682 | 3.2 | 3.6818 | 3.2 | 4.2955 | 3.2 | 4.9091 | 3.2 | 5.5227 | 3.2 | 6.1364
3.3 | 0.29348 | 3.3 | 0.58696 | 3.3 | 1.1739 | 3.3 | 1.7609 | 3.3 | 2.3478 | 3.3 | 2.9348 | 3.3 | 3.5217 | 3.3 | 4.1087 | 3.3 | 4.6957 | 3.3 | 5.2826 | 3.3 | 5.8696
3.4 | 0.28125 | 3.4 | 0.5625 | 3.4 | 1.125 | 3.4 | 1.6875 | 3.4 | 2.25 | 3.4 | 2.8125 | 3.4 | 3.375 | 3.4 | 3.9375 | 3.4 | 4.5 | 3.4 | 5.0625 | 3.4 | 5.625
3.5 | 0.27 | 3.5 | 0.54 | 3.5 | 1.08 | 3.5 | 1.62 | 3.5 | 2.16 | 3.5 | 2.7 | 3.5 | 3.24 | 3.5 | 3.78 | 3.5 | 4.32 | 3.5 | 4.86 | 3.5 | 5.4
3.6 | 0.25962 | 3.6 | 0.51923 | 3.6 | 1.0385 | 3.6 | 1.5577 | 3.6 | 2.0769 | 3.6 | 2.5962 | 3.6 | 3.1154 | 3.6 | 3.6346 | 3.6 | 4.1538 | 3.6 | 4.6731 | 3.6 | 5.1923
3.7 | 0.25 | 3.7 | 0.5 | 3.7 | 1 | 3.7 | 1.5 | 3.7 | 2 | 3.7 | 2.5 | 3.7 | 3 | 3.7 | 3.5 | 3.7 | 4 | 3.7 | 4.5 | 3.7 | 5
3.8 | 0.24107 | 3.8 | 0.48214 | 3.8 | 0.96429 | 3.8 | 1.4464 | 3.8 | 1.9286 | 3.8 | 2.4107 | 3.8 | 2.8929 | 3.8 | 3.375 | 3.8 | 3.8571 | 3.8 | 4.3393 | 3.8 | 4.8214
3.9 | 0.23276 | 3.9 | 0.46552 | 3.9 | 0.93103 | 3.9 | 1.3966 | 3.9 | 1.8621 | 3.9 | 2.3276 | 3.9 | 2.7931 | 3.9 | 3.2586 | 3.9 | 3.7241 | 3.9 | 4.1897 | 3.9 | 4.6552
4 | 0.225 | 4 | 0.45 | 4 | 0.9 | 4 | 1.35 | 4 | 1.8 | 4 | 2.25 | 4 | 2.7 | 4 | 3.15 | 4 | 3.6 | 4 | 4.05 | 4 | 4.5
4.1 | 0.21774 | 4.1 | 0.43548 | 4.1 | 0.87097 | 4.1 | 1.3065 | 4.1 | 1.7419 | 4.1 | 2.1774 | 4.1 | 2.6129 | 4.1 | 3.0484 | 4.1 | 3.4839 | 4.1 | 3.9194 | 4.1 | 4.3548
4.2 | 0.21094 | 4.2 | 0.42188 | 4.2 | 0.84375 | 4.2 | 1.2656 | 4.2 | 1.6875 | 4.2 | 2.1094 | 4.2 | 2.5312 | 4.2 | 2.9531 | 4.2 | 3.375 | 4.2 | 3.7969 | 4.2 | 4.2188
4.3 | 0.20455 | 4.3 | 0.40909 | 4.3 | 0.81818 | 4.3 | 1.2273 | 4.3 | 1.6364 | 4.3 | 2.0455 | 4.3 | 2.4545 | 4.3 | 2.8636 | 4.3 | 3.2727 | 4.3 | 3.6818 | 4.3 | 4.0909
4.4 | 0.19853 | 4.4 | 0.39706 | 4.4 | 0.79412 | 4.4 | 1.1912 | 4.4 | 1.5882 | 4.4 | 1.9853 | 4.4 | 2.3824 | 4.4 | 2.7794 | 4.4 | 3.1765 | 4.4 | 3.5735 | 4.4 | 3.9706
4.5 | 0.19286 | 4.5 | 0.38571 | 4.5 | 0.77143 | 4.5 | 1.1571 | 4.5 | 1.5429 | 4.5 | 1.9286 | 4.5 | 2.3143 | 4.5 | 2.7 | 4.5 | 3.0857 | 4.5 | 3.4714 | 4.5 | 3.8571
4.6 | 0.1875 | 4.6 | 0.375 | 4.6 | 0.75 | 4.6 | 1.125 | 4.6 | 1.5 | 4.6 | 1.875 | 4.6 | 2.25 | 4.6 | 2.625 | 4.6 | 3 | 4.6 | 3.375 | 4.6 | 3.75
4.7 | 0.18243 | 4.7 | 0.36486 | 4.7 | 0.72973 | 4.7 | 1.0946 | 4.7 | 1.4595 | 4.7 | 1.8243 | 4.7 | 2.1892 | 4.7 | 2.5541 | 4.7 | 2.9189 | 4.7 | 3.2838 | 4.7 | 3.6486
4.8 | 0.17763 | 4.8 | 0.35526 | 4.8 | 0.71053 | 4.8 | 1.0658 | 4.8 | 1.4211 | 4.8 | 1.7763 | 4.8 | 2.1316 | 4.8 | 2.4868 | 4.8 | 2.8421 | 4.8 | 3.1974 | 4.8 | 3.5526
4.9 | 0.17308 | 4.9 | 0.34615 | 4.9 | 0.69231 | 4.9 | 1.0385 | 4.9 | 1.3846 | 4.9 | 1.7308 | 4.9 | 2.0769 | 4.9 | 2.4231 | 4.9 | 2.7692 | 4.9 | 3.1154 | 4.9 | 3.4615
5 | 0.16875 | 5 | 0.3375 | 5 | 0.675 | 5 | 1.0125 | 5 | 1.35 | 5 | 1.6875 | 5 | 2.025 | 5 | 2.3625 | 5 | 2.7 | 5 | 3.0375 | 5 | 3.375
5.1 | 0.16463 | 5.1 | 0.32927 | 5.1 | 0.65854 | 5.1 | 0.9878 | 5.1 | 1.3171 | 5.1 | 1.6463 | 5.1 | 1.9756 | 5.1 | 2.3049 | 5.1 | 2.6341 | 5.1 | 2.9634 | 5.1 | 3.2927
5.2 | 0.16071 | 5.2 | 0.32143 | 5.2 | 0.64286 | 5.2 | 0.96429 | 5.2 | 1.2857 | 5.2 | 1.6071 | 5.2 | 1.9286 | 5.2 | 2.25 | 5.2 | 2.5714 | 5.2 | 2.8929 | 5.2 | 3.2143
5.3 | 0.15698 | 5.3 | 0.31395 | 5.3 | 0.62791 | 5.3 | 0.94186 | 5.3 | 1.2558 | 5.3 | 1.5698 | 5.3 | 1.8837 | 5.3 | 2.1977 | 5.3 | 2.5116 | 5.3 | 2.8256 | 5.3 | 3.1395
5.4 | 0.15341 | 5.4 | 0.30682 | 5.4 | 0.61364 | 5.4 | 0.92045 | 5.4 | 1.2273 | 5.4 | 1.5341 | 5.4 | 1.8409 | 5.4 | 2.1477 | 5.4 | 2.4545 | 5.4 | 2.7614 | 5.4 | 3.0682
5.5 | 0.15 | 5.5 | 0.3 | 5.5 | 0.6 | 5.5 | 0.9 | 5.5 | 1.2 | 5.5 | 1.5 | 5.5 | 1.8 | 5.5 | 2.1 | 5.5 | 2.4 | 5.5 | 2.7 | 5.5 | 3
5.6 | 0.14674 | 5.6 | 0.29348 | 5.6 | 0.58696 | 5.6 | 0.88043 | 5.6 | 1.1739 | 5.6 | 1.4674 | 5.6 | 1.7609 | 5.6 | 2.0543 | 5.6 | 2.3478 | 5.6 | 2.6413 | 5.6 | 2.9348
5.7 | 0.14362 | 5.7 | 0.28723 | 5.7 | 0.57447 | 5.7 | 0.8617 | 5.7 | 1.1489 | 5.7 | 1.4362 | 5.7 | 1.7234 | 5.7 | 2.0106 | 5.7 | 2.2979 | 5.7 | 2.5851 | 5.7 | 2.8723
5.8 | 0.14062 | 5.8 | 0.28125 | 5.8 | 0.5625 | 5.8 | 0.84375 | 5.8 | 1.125 | 5.8 | 1.4062 | 5.8 | 1.6875 | 5.8 | 1.9688 | 5.8 | 2.25 | 5.8 | 2.5312 | 5.8 | 2.8125
5.9 | 0.13776 | 5.9 | 0.27551 | 5.9 | 0.55102 | 5.9 | 0.82653 | 5.9 | 1.102 | 5.9 | 1.3776 | 5.9 | 1.6531 | 5.9 | 1.9286 | 5.9 | 2.2041 | 5.9 | 2.4796 | 5.9 | 2.7551
6 | 0.135 | 6 | 0.27 | 6 | 0.54 | 6 | 0.81 | 6 | 1.08 | 6 | 1.35 | 6 | 1.62 | 6 | 1.89 | 6 | 2.16 | 6 | 2.43 | 6 | 2.7
6.1 | 0.13235 | 6.1 | 0.26471 | 6.1 | 0.52941 | 6.1 | 0.79412 | 6.1 | 1.0588 | 6.1 | 1.3235 | 6.1 | 1.5882 | 6.1 | 1.8529 | 6.1 | 2.1176 | 6.1 | 2.3824 | 6.1 | 2.6471
6.2 | 0.12981 | 6.2 | 0.25962 | 6.2 | 0.51923 | 6.2 | 0.77885 | 6.2 | 1.0385 | 6.2 | 1.2981 | 6.2 | 1.5577 | 6.2 | 1.8173 | 6.2 | 2.0769 | 6.2 | 2.3365 | 6.2 | 2.5962
6.3 | 0.12736 | 6.3 | 0.25472 | 6.3 | 0.50943 | 6.3 | 0.76415 | 6.3 | 1.0189 | 6.3 | 1.2736 | 6.3 | 1.5283 | 6.3 | 1.783 | 6.3 | 2.0377 | 6.3 | 2.2925 | 6.3 | 2.5472
6.4 | 0.125 | 6.4 | 0.25 | 6.4 | 0.5 | 6.4 | 0.75 | 6.4 | 1 | 6.4 | 1.25 | 6.4 | 1.5 | 6.4 | 1.75 | 6.4 | 2 | 6.4 | 2.25 | 6.4 | 2.5
6.5 | 0.12273 | 6.5 | 0.24545 | 6.5 | 0.49091 | 6.5 | 0.73636 | 6.5 | 0.98182 | 6.5 | 1.2273 | 6.5 | 1.4727 | 6.5 | 1.7182 | 6.5 | 1.9636 | 6.5 | 2.2091 | 6.5 | 2.4545
6.6 | 0.12054 | 6.6 | 0.24107 | 6.6 | 0.48214 | 6.6 | 0.72321 | 6.6 | 0.96429 | 6.6 | 1.2054 | 6.6 | 1.4464 | 6.6 | 1.6875 | 6.6 | 1.9286 | 6.6 | 2.1696 | 6.6 | 2.4107
6.7 | 0.11842 | 6.7 | 0.23684 | 6.7 | 0.47368 | 6.7 | 0.71053 | 6.7 | 0.94737 | 6.7 | 1.1842 | 6.7 | 1.4211 | 6.7 | 1.6579 | 6.7 | 1.8947 | 6.7 | 2.1316 | 6.7 | 2.3684
6.8 | 0.11638 | 6.8 | 0.23276 | 6.8 | 0.46552 | 6.8 | 0.69828 | 6.8 | 0.93103 | 6.8 | 1.1638 | 6.8 | 1.3966 | 6.8 | 1.6293 | 6.8 | 1.8621 | 6.8 | 2.0948 | 6.8 | 2.3276
6.9 | 0.11441 | 6.9 | 0.22881 | 6.9 | 0.45763 | 6.9 | 0.68644 | 6.9 | 0.91525 | 6.9 | 1.1441 | 6.9 | 1.3729 | 6.9 | 1.6017 | 6.9 | 1.8305 | 6.9 | 2.0593 | 6.9 | 2.2881
7 | 0.1125 | 7 | 0.225 | 7 | 0.45 | 7 | 0.675 | 7 | 0.9 | 7 | 1.125 | 7 | 1.35 | 7 | 1.575 | 7 | 1.8 | 7 | 2.025 | 7 | 2.25
7.1 | 0.11066 | 7.1 | 0.22131 | 7.1 | 0.44262 | 7.1 | 0.66393 | 7.1 | 0.88525 | 7.1 | 1.1066 | 7.1 | 1.3279 | 7.1 | 1.5492 | 7.1 | 1.7705 | 7.1 | 1.9918 | 7.1 | 2.2131
7.2 | 0.10887 | 7.2 | 0.21774 | 7.2 | 0.43548 | 7.2 | 0.65323 | 7.2 | 0.87097 | 7.2 | 1.0887 | 7.2 | 1.3065 | 7.2 | 1.5242 | 7.2 | 1.7419 | 7.2 | 1.9597 | 7.2 | 2.1774
7.3 | 0.10714 | 7.3 | 0.21429 | 7.3 | 0.42857 | 7.3 | 0.64286 | 7.3 | 0.85714 | 7.3 | 1.0714 | 7.3 | 1.2857 | 7.3 | 1.5 | 7.3 | 1.7143 | 7.3 | 1.9286 | 7.3 | 2.1429
7.4 | 0.10547 | 7.4 | 0.21094 | 7.4 | 0.42188 | 7.4 | 0.63281 | 7.4 | 0.84375 | 7.4 | 1.0547 | 7.4 | 1.2656 | 7.4 | 1.4766 | 7.4 | 1.6875 | 7.4 | 1.8984 | 7.4 | 2.1094
7.5 | 0.10385 | 7.5 | 0.20769 | 7.5 | 0.41538 | 7.5 | 0.62308 | 7.5 | 0.83077 | 7.5 | 1.0385 | 7.5 | 1.2462 | 7.5 | 1.4538 | 7.5 | 1.6615 | 7.5 | 1.8692 | 7.5 | 2.0769
7.6 | 0.10227 | 7.6 | 0.20455 | 7.6 | 0.40909 | 7.6 | 0.61364 | 7.6 | 0.81818 | 7.6 | 1.0227 | 7.6 | 1.2273 | 7.6 | 1.4318 | 7.6 | 1.6364 | 7.6 | 1.8409 | 7.6 | 2.0455
7.7 | 0.10075 | 7.7 | 0.20149 | 7.7 | 0.40299 | 7.7 | 0.60448 | 7.7 | 0.80597 | 7.7 | 1.0075 | 7.7 | 1.209 | 7.7 | 1.4104 | 7.7 | 1.6119 | 7.7 | 1.8134 | 7.7 | 2.0149
7.8 | 0.099265 | 7.8 | 0.19853 | 7.8 | 0.39706 | 7.8 | 0.59559 | 7.8 | 0.79412 | 7.8 | 0.99265 | 7.8 | 1.1912 | 7.8 | 1.3897 | 7.8 | 1.5882 | 7.8 | 1.7868 | 7.8 | 1.9853
7.9 | 0.097826 | 7.9 | 0.19565 | 7.9 | 0.3913 | 7.9 | 0.58696 | 7.9 | 0.78261 | 7.9 | 0.97826 | 7.9 | 1.1739 | 7.9 | 1.3696 | 7.9 | 1.5652 | 7.9 | 1.7609 | 7.9 | 1.9565
8 | 0.096429 | 8 | 0.19286 | 8 | 0.38571 | 8 | 0.57857 | 8 | 0.77143 | 8 | 0.96429 | 8 | 1.1571 | 8 | 1.35 | 8 | 1.5429 | 8 | 1.7357 | 8 | 1.9286
8.1 | 0.09507 | 8.1 | 0.19014 | 8.1 | 0.38028 | 8.1 | 0.57042 | 8.1 | 0.76056 | 8.1 | 0.9507 | 8.1 | 1.1408 | 8.1 | 1.331 | 8.1 | 1.5211 | 8.1 | 1.7113 | 8.1 | 1.9014
8.2 | 0.09375 | 8.2 | 0.1875 | 8.2 | 0.375 | 8.2 | 0.5625 | 8.2 | 0.75 | 8.2 | 0.9375 | 8.2 | 1.125 | 8.2 | 1.3125 | 8.2 | 1.5 | 8.2 | 1.6875 | 8.2 | 1.875
8.3 | 0.092466 | 8.3 | 0.18493 | 8.3 | 0.36986 | 8.3 | 0.55479 | 8.3 | 0.73973 | 8.3 | 0.92466 | 8.3 | 1.1096 | 8.3 | 1.2945 | 8.3 | 1.4795 | 8.3 | 1.6644 | 8.3 | 1.8493
8.4 | 0.091216 | 8.4 | 0.18243 | 8.4 | 0.36486 | 8.4 | 0.5473 | 8.4 | 0.72973 | 8.4 | 0.91216 | 8.4 | 1.0946 | 8.4 | 1.277 | 8.4 | 1.4595 | 8.4 | 1.6419 | 8.4 | 1.8243
8.5 | 0.09 | 8.5 | 0.18 | 8.5 | 0.36 | 8.5 | 0.54 | 8.5 | 0.72 | 8.5 | 0.9 | 8.5 | 1.08 | 8.5 | 1.26 | 8.5 | 1.44 | 8.5 | 1.62 | 8.5 | 1.8
8.6 | 0.088816 | 8.6 | 0.17763 | 8.6 | 0.35526 | 8.6 | 0.53289 | 8.6 | 0.71053 | 8.6 | 0.88816 | 8.6 | 1.0658 | 8.6 | 1.2434 | 8.6 | 1.4211 | 8.6 | 1.5987 | 8.6 | 1.7763
8.7 | 0.087662 | 8.7 | 0.17532 | 8.7 | 0.35065 | 8.7 | 0.52597 | 8.7 | 0.7013 | 8.7 | 0.87662 | 8.7 | 1.0519 | 8.7 | 1.2273 | 8.7 | 1.4026 | 8.7 | 1.5779 | 8.7 | 1.7532
8.8 | 0.086538 | 8.8 | 0.17308 | 8.8 | 0.34615 | 8.8 | 0.51923 | 8.8 | 0.69231 | 8.8 | 0.86538 | 8.8 | 1.0385 | 8.8 | 1.2115 | 8.8 | 1.3846 | 8.8 | 1.5577 | 8.8 | 1.7308
8.9 | 0.085443 | 8.9 | 0.17089 | 8.9 | 0.34177 | 8.9 | 0.51266 | 8.9 | 0.68354 | 8.9 | 0.85443 | 8.9 | 1.0253 | 8.9 | 1.1962 | 8.9 | 1.3671 | 8.9 | 1.538 | 8.9 | 1.7089
9 | 0.084375 | 9 | 0.16875 | 9 | 0.3375 | 9 | 0.50625 | 9 | 0.675 | 9 | 0.84375 | 9 | 1.0125 | 9 | 1.1812 | 9 | 1.35 | 9 | 1.5188 | 9 | 1.6875
9.1 | 0.083333 | 9.1 | 0.16667 | 9.1 | 0.33333 | 9.1 | 0.5 | 9.1 | 0.66667 | 9.1 | 0.83333 | 9.1 | 1 | 9.1 | 1.1667 | 9.1 | 1.3333 | 9.1 | 1.5 | 9.1 | 1.6667
9.2 | 0.082317 | 9.2 | 0.16463 | 9.2 | 0.32927 | 9.2 | 0.4939 | 9.2 | 0.65854 | 9.2 | 0.82317 | 9.2 | 0.9878 | 9.2 | 1.1524 | 9.2 | 1.3171 | 9.2 | 1.4817 | 9.2 | 1.6463
9.3 | 0.081325 | 9.3 | 0.16265 | 9.3 | 0.3253 | 9.3 | 0.48795 | 9.3 | 0.6506 | 9.3 | 0.81325 | 9.3 | 0.9759 | 9.3 | 1.1386 | 9.3 | 1.3012 | 9.3 | 1.4639 | 9.3 | 1.6265
9.4 | 0.080357 | 9.4 | 0.16071 | 9.4 | 0.32143 | 9.4 | 0.48214 | 9.4 | 0.64286 | 9.4 | 0.80357 | 9.4 | 0.96429 | 9.4 | 1.125 | 9.4 | 1.2857 | 9.4 | 1.4464 | 9.4 | 1.6071
9.5 | 0.079412 | 9.5 | 0.15882 | 9.5 | 0.31765 | 9.5 | 0.47647 | 9.5 | 0.63529 | 9.5 | 0.79412 | 9.5 | 0.95294 | 9.5 | 1.1118 | 9.5 | 1.2706 | 9.5 | 1.4294 | 9.5 | 1.5882
9.6 | 0.078488 | 9.6 | 0.15698 | 9.6 | 0.31395 | 9.6 | 0.47093 | 9.6 | 0.62791 | 9.6 | 0.78488 | 9.6 | 0.94186 | 9.6 | 1.0988 | 9.6 | 1.2558 | 9.6 | 1.4128 | 9.6 | 1.5698
9.7 | 0.077586 | 9.7 | 0.15517 | 9.7 | 0.31034 | 9.7 | 0.46552 | 9.7 | 0.62069 | 9.7 | 0.77586 | 9.7 | 0.93103 | 9.7 | 1.0862 | 9.7 | 1.2414 | 9.7 | 1.3966 | 9.7 | 1.5517
9.8 | 0.076705 | 9.8 | 0.15341 | 9.8 | 0.30682 | 9.8 | 0.46023 | 9.8 | 0.61364 | 9.8 | 0.76705 | 9.8 | 0.92045 | 9.8 | 1.0739 | 9.8 | 1.2273 | 9.8 | 1.3807 | 9.8 | 1.5341
9.9 | 0.075843 | 9.9 | 0.15169 | 9.9 | 0.30337 | 9.9 | 0.45506 | 9.9 | 0.60674 | 9.9 | 0.75843 | 9.9 | 0.91011 | 9.9 | 1.0618 | 9.9 | 1.2135 | 9.9 | 1.3652 | 9.9 | 1.5169
10 | 0.075 | 10 | 0.15 | 10 | 0.3 | 10 | 0.45 | 10 | 0.6 | 10 | 0.75 | 10 | 0.9 | 10 | 1.05 | 10 | 1.2 | 10 | 1.35 | 10 | 1.5
10.5 | 0.071053 | 10.5 | 0.14211 | 10.5 | 0.28421 | 10.5 | 0.42632 | 10.5 | 0.56842 | 10.5 | 0.71053 | 10.5 | 0.85263 | 10.5 | 0.99474 | 10.5 | 1.1368 | 10.5 | 1.2789 | 10.5 | 1.4211
11 | 0.0675 | 11 | 0.135 | 11 | 0.27 | 11 | 0.405 | 11 | 0.54 | 11 | 0.675 | 11 | 0.81 | 11 | 0.945 | 11 | 1.08 | 11 | 1.215 | 11 | 1.35
11.5 | 0.064286 | 11.5 | 0.12857 | 11.5 | 0.25714 | 11.5 | 0.38571 | 11.5 | 0.51429 | 11.5 | 0.64286 | 11.5 | 0.77143 | 11.5 | 0.9 | 11.5 | 1.0286 | 11.5 | 1.1571 | 11.5 | 1.2857
12 | 0.061364 | 12 | 0.12273 | 12 | 0.24545 | 12 | 0.36818 | 12 | 0.49091 | 12 | 0.61364 | 12 | 0.73636 | 12 | 0.85909 | 12 | 0.98182 | 12 | 1.1045 | 12 | 1.2273
12.5 | 0.058696 | 12.5 | 0.11739 | 12.5 | 0.23478 | 12.5 | 0.35217 | 12.5 | 0.46957 | 12.5 | 0.58696 | 12.5 | 0.70435 | 12.5 | 0.82174 | 12.5 | 0.93913 | 12.5 | 1.0565 | 12.5 | 1.1739
13 | 0.05625 | 13 | 0.1125 | 13 | 0.225 | 13 | 0.3375 | 13 | 0.45 | 13 | 0.5625 | 13 | 0.675 | 13 | 0.7875 | 13 | 0.9 | 13 | 1.0125 | 13 | 1.125
13.5 | 0.054 | 13.5 | 0.108 | 13.5 | 0.216 | 13.5 | 0.324 | 13.5 | 0.432 | 13.5 | 0.54 | 13.5 | 0.648 | 13.5 | 0.756 | 13.5 | 0.864 | 13.5 | 0.972 | 13.5 | 1.08
14 | 0.051923 | 14 | 0.10385 | 14 | 0.20769 | 14 | 0.31154 | 14 | 0.41538 | 14 | 0.51923 | 14 | 0.62308 | 14 | 0.72692 | 14 | 0.83077 | 14 | 0.93462 | 14 | 1.0385
14.5 | 0.05 | 14.5 | 0.1 | 14.5 | 0.2 | 14.5 | 0.3 | 14.5 | 0.4 | 14.5 | 0.5 | 14.5 | 0.6 | 14.5 | 0.7 | 14.5 | 0.8 | 14.5 | 0.9 | 14.5 | 1
15 | 0.048214 | 15 | 0.096429 | 15 | 0.19286 | 15 | 0.28929 | 15 | 0.38571 | 15 | 0.48214 | 15 | 0.57857 | 15 | 0.675 | 15 | 0.77143 | 15 | 0.86786 | 15 | 0.96429
16 | 0.045 | 16 | 0.09 | 16 | 0.18 | 16 | 0.27 | 16 | 0.36 | 16 | 0.45 | 16 | 0.54 | 16 | 0.63 | 16 | 0.72 | 16 | 0.81 | 16 | 0.9
17 | 0.042188 | 17 | 0.084375 | 17 | 0.16875 | 17 | 0.25312 | 17 | 0.3375 | 17 | 0.42188 | 17 | 0.50625 | 17 | 0.59062 | 17 | 0.675 | 17 | 0.75938 | 17 | 0.84375
18 | 0.039706 | 18 | 0.079412 | 18 | 0.15882 | 18 | 0.23824 | 18 | 0.31765 | 18 | 0.39706 | 18 | 0.47647 | 18 | 0.55588 | 18 | 0.63529 | 18 | 0.71471 | 18 | 0.79412
19 | 0.0375 | 19 | 0.075 | 19 | 0.15 | 19 | 0.225 | 19 | 0.3 | 19 | 0.375 | 19 | 0.45 | 19 | 0.525 | 19 | 0.6 | 19 | 0.675 | 19 | 0.75
20 | 0.035526 | 20 | 0.071053 | 20 | 0.14211 | 20 | 0.21316 | 20 | 0.28421 | 20 | 0.35526 | 20 | 0.42632 | 20 | 0.49737 | 20 | 0.56842 | 20 | 0.63947 | 20 | 0.71053
21 | 0.03375 | 21 | 0.0675 | 21 | 0.135 | 21 | 0.2025 | 21 | 0.27 | 21 | 0.3375 | 21 | 0.405 | 21 | 0.4725 | 21 | 0.54 | 21 | 0.6075 | 21 | 0.675
22 | 0.032143 | 22 | 0.064286 | 22 | 0.12857 | 22 | 0.19286 | 22 | 0.25714 | 22 | 0.32143 | 22 | 0.38571 | 22 | 0.45 | 22 | 0.51429 | 22 | 0.57857 | 22 | 0.64286
23 | 0.030682 | 23 | 0.061364 | 23 | 0.12273 | 23 | 0.18409 | 23 | 0.24545 | 23 | 0.30682 | 23 | 0.36818 | 23 | 0.42955 | 23 | 0.49091 | 23 | 0.55227 | 23 | 0.61364
24 | 0.029348 | 24 | 0.058696 | 24 | 0.11739 | 24 | 0.17609 | 24 | 0.23478 | 24 | 0.29348 | 24 | 0.35217 | 24 | 0.41087 | 24 | 0.46957 | 24 | 0.52826 | 24 | 0.58696
25 | 0.028125 | 25 | 0.05625 | 25 | 0.1125 | 25 | 0.16875 | 25 | 0.225 | 25 | 0.28125 | 25 | 0.3375 | 25 | 0.39375 | 25 | 0.45 | 25 | 0.50625 | 25 | 0.5625
26 | 0.027 | 26 | 0.054 | 26 | 0.108 | 26 | 0.162 | 26 | 0.216 | 26 | 0.27 | 26 | 0.324 | 26 | 0.378 | 26 | 0.432 | 26 | 0.486 | 26 | 0.54
27 | 0.025962 | 27 | 0.051923 | 27 | 0.10385 | 27 | 0.15577 | 27 | 0.20769 | 27 | 0.25962 | 27 | 0.31154 | 27 | 0.36346 | 27 | 0.41538 | 27 | 0.46731 | 27 | 0.51923
28 | 0.025 | 28 | 0.05 | 28 | 0.1 | 28 | 0.15 | 28 | 0.2 | 28 | 0.25 | 28 | 0.3 | 28 | 0.35 | 28 | 0.4 | 28 | 0.45 | 28 | 0.5
29 | 0.024107 | 29 | 0.048214 | 29 | 0.096429 | 29 | 0.14464 | 29 | 0.19286 | 29 | 0.24107 | 29 | 0.28929 | 29 | 0.3375 | 29 | 0.38571 | 29 | 0.43393 | 29 | 0.48214
30 | 0.023276 | 30 | 0.046552 | 30 | 0.093103 | 30 | 0.13966 | 30 | 0.18621 | 30 | 0.23276 | 30 | 0.27931 | 30 | 0.32586 | 30 | 0.37241 | 30 | 0.41897 | 30 | 0.46552
31 | 0.023276 | 31 | 0.046552 | 31 | 0.093103 | 31 | 0.13966 | 31 | 0.18621 | 31 | 0.23276 | 31 | 0.27931 | 31 | 0.32586 | 31 | 0.37241 | 31 | 0.41897 | 31 | 0.46552
32 | 0.023276 | 32 | 0.046552 | 32 | 0.093103 | 32 | 0.13966 | 32 | 0.18621 | 32 | 0.23276 | 32 | 0.27931 | 32 | 0.32586 | 32 | 0.37241 | 32 | 0.41897 | 32 | 0.46552
33 | 0.023276 | 33 | 0.046552 | 33 | 0.093103 | 33 | 0.13966 | 33 | 0.18621 | 33 | 0.23276 | 33 | 0.27931 | 33 | 0.32586 | 33 | 0.37241 | 33 | 0.41897 | 33 | 0.46552
34 | 0.023276 | 34 | 0.046552 | 34 | 0.093103 | 34 | 0.13966 | 34 | 0.18621 | 34 | 0.23276 | 34 | 0.27931 | 34 | 0.32586 | 34 | 0.37241 | 34 | 0.41897 | 34 | 0.46552
35 | 0.023276 | 35 | 0.046552 | 35 | 0.093103 | 35 | 0.13966 | 35 | 0.18621 | 35 | 0.23276 | 35 | 0.27931 | 35 | 0.32586 | 35 | 0.37241 | 35 | 0.41897 | 35 | 0.46552
36 | 0.023276 | 36 | 0.046552 | 36 | 0.093103 | 36 | 0.13966 | 36 | 0.18621 | 36 | 0.23276 | 36 | 0.27931 | 36 | 0.32586 | 36 | 0.37241 | 36 | 0.41897 | 36 | 0.46552
37 | 0.023276 | 37 | 0.046552 | 37 | 0.093103 | 37 | 0.13966 | 37 | 0.18621 | 37 | 0.23276 | 37 | 0.27931 | 37 | 0.32586 | 37 | 0.37241 | 37 | 0.41897 | 37 | 0.46552
38 | 0.023276 | 38 | 0.046552 | 38 | 0.093103 | 38 | 0.13966 | 38 | 0.18621 | 38 | 0.23276 | 38 | 0.27931 | 38 | 0.32586 | 38 | 0.37241 | 38 | 0.41897 | 38 | 0.46552
39 | 0.023276 | 39 | 0.046552 | 39 | 0.093103 | 39 | 0.13966 | 39 | 0.18621 | 39 | 0.23276 | 39 | 0.27931 | 39 | 0.32586 | 39 | 0.37241 | 39 | 0.41897 | 39 | 0.46552
40 | 0.023276 | 40 | 0.046552 | 40 | 0.093103 | 40 | 0.13966 | 40 | 0.18621 | 40 | 0.23276 | 40 | 0.27931 | 40 | 0.32586 | 40 | 0.37241 | 40 | 0.41897 | 40 | 0.46552
41 | 0.023276 | 41 | 0.046552 | 41 | 0.093103 | 41 | 0.13966 | 41 | 0.18621 | 41 | 0.23276 | 41 | 0.27931 | 41 | 0.32586 | 41 | 0.37241 | 41 | 0.41897 | 41 | 0.46552
42 | 0.023276 | 42 | 0.046552 | 42 | 0.093103 | 42 | 0.13966 | 42 | 0.18621 | 42 | 0.23276 | 42 | 0.27931 | 42 | 0.32586 | 42 | 0.37241 | 42 | 0.41897 | 42 | 0.46552
43 | 0.023276 | 43 | 0.046552 | 43 | 0.093103 | 43 | 0.13966 | 43 | 0.18621 | 43 | 0.23276 | 43 | 0.27931 | 43 | 0.32586 | 43 | 0.37241 | 43 | 0.41897 | 43 | 0.46552
44 | 0.023276 | 44 | 0.046552 | 44 | 0.093103 | 44 | 0.13966 | 44 | 0.18621 | 44 | 0.23276 | 44 | 0.27931 | 44 | 0.32586 | 44 | 0.37241 | 44 | 0.41897 | 44 | 0.46552
45 | 0.023276 | 45 | 0.046552 | 45 | 0.093103 | 45 | 0.13966 | 45 | 0.18621 | 45 | 0.23276 | 45 | 0.27931 | 45 | 0.32586 | 45 | 0.37241 | 45 | 0.41897 | 45 | 0.46552
46 | 0.023276 | 46 | 0.046552 | 46 | 0.093103 | 46 | 0.13966 | 46 | 0.18621 | 46 | 0.23276 | 46 | 0.27931 | 46 | 0.32586 | 46 | 0.37241 | 46 | 0.41897 | 46 | 0.46552
47 | 0.023276 | 47 | 0.046552 | 47 | 0.093103 | 47 | 0.13966 | 47 | 0.18621 | 47 | 0.23276 | 47 | 0.27931 | 47 | 0.32586 | 47 | 0.37241 | 47 | 0.41897 | 47 | 0.46552
48 | 0.023276 | 48 | 0.046552 | 48 | 0.093103 | 48 | 0.13966 | 48 | 0.18621 | 48 | 0.23276 | 48 | 0.27931 | 48 | 0.32586 | 48 | 0.37241 | 48 | 0.41897 | 48 | 0.46552
49 | 0.023276 | 49 | 0.046552 | 49 | 0.093103 | 49 | 0.13966 | 49 | 0.18621 | 49 | 0.23276 | 49 | 0.27931 | 49 | 0.32586 | 49 | 0.37241 | 49 | 0.41897 | 49 | 0.46552
50 | 0.023276 | 50 | 0.046552 | 50 | 0.093103 | 50 | 0.13966 | 50 | 0.18621 | 50 | 0.23276 | 50 | 0.27931 | 50 | 0.32586 | 50 | 0.37241 | 50 | 0.41897 | 50 | 0.46552
55 | 0.023276 | 55 | 0.046552 | 55 | 0.093103 | 55 | 0.13966 | 55 | 0.18621 | 55 | 0.23276 | 55 | 0.27931 | 55 | 0.32586 | 55 | 0.37241 | 55 | 0.41897 | 55 | 0.46552
60 | 0.023276 | 60 | 0.046552 | 60 | 0.093103 | 60 | 0.13966 | 60 | 0.18621 | 60 | 0.23276 | 60 | 0.27931 | 60 | 0.32586 | 60 | 0.37241 | 60 | 0.41897 | 60 | 0.46552
65 | 0.023276 | 65 | 0.046552 | 65 | 0.093103 | 65 | 0.13966 | 65 | 0.18621 | 65 | 0.23276 | 65 | 0.27931 | 65 | 0.32586 | 65 | 0.37241 | 65 | 0.41897 | 65 | 0.46552
70 | 0.023276 | 70 | 0.046552 | 70 | 0.093103 | 70 | 0.13966 | 70 | 0.18621 | 70 | 0.23276 | 70 | 0.27931 | 70 | 0.32586 | 70 | 0.37241 | 70 | 0.41897 | 70 | 0.46552
75 | 0.023276 | 75 | 0.046552 | 75 | 0.093103 | 75 | 0.13966 | 75 | 0.18621 | 75 | 0.23276 | 75 | 0.27931 | 75 | 0.32586 | 75 | 0.37241 | 75 | 0.41897 | 75 | 0.46552
80 | 0.023276 | 80 | 0.046552 | 80 | 0.093103 | 80 | 0.13966 | 80 | 0.18621 | 80 | 0.23276 | 80 | 0.27931 | 80 | 0.32586 | 80 | 0.37241 | 80 | 0.41897 | 80 | 0.46552
85 | 0.023276 | 85 | 0.046552 | 85 | 0.093103 | 85 | 0.13966 | 85 | 0.18621 | 85 | 0.23276 | 85 | 0.27931 | 85 | 0.32586 | 85 | 0.37241 | 85 | 0.41897 | 85 | 0.46552
90 | 0.023276 | 90 | 0.046552 | 90 | 0.093103 | 90 | 0.13966 | 90 | 0.18621 | 90 | 0.23276 | 90 | 0.27931 | 90 | 0.32586 | 90 | 0.37241 | 90 | 0.41897 | 90 | 0.46552
95 | 0.023276 | 95 | 0.046552 | 95 | 0.093103 | 95 | 0.13966 | 95 | 0.18621 | 95 | 0.23276 | 95 | 0.27931 | 95 | 0.32586 | 95 | 0.37241 | 95 | 0.41897 | 95 | 0.46552
100 | 0.023276 | 100 | 0.046552 | 100 | 0.093103 | 100 | 0.13966 | 100 | 0.18621 | 100 | 0.23276 | 100 | 0.27931 | 100 | 0.32586 | 100 | 0.37241 | 100 | 0.41897 | 100 | 0.46552